## Sheet1
REF615 Relay Current Protection |  |  | REF615 Relay Voltage Protection
S.N | INRPHAR1 |  | S.N | PHPTOV1
1 | Operation | ON | 1 | Operation | ON
2 | Start Value | 20% | 2 | Number of start Phase | 1 Out of 3
3 | Operation Delay time | 20 ms | 3 | Start Value | 1.10 un
4 | Reset Delay time | 20 ms | 4 | Operation Delay time | 300 MS
| EFHPTOC1 |  | 5 | Reset Delay time | 20 MS
1 | Operation | ON | 6 | Operation Curve tye | IFC DEF TIME
2 | Start Value | 0.10 IN | 7 | Voltage Selection | Phase to Phase
3 | Start Value multi | 1 | 8 | Reative Hysteresis | 4%
4 | Operation Delay time | 310 ms
5 | Reset Delay time | 20 ms
6 | Operation Curve tye | IEC DEF. Time
7 | Mesurment Mode | DFT
8 | IO Signal se | IO
DEFLPDEF1
1 | Operation | ON
2 | Start Value | 0.045 IN
3 | Start Value multi | 1
4 | Directon Mode | Non Directioal
5 | Time Multiplier | 0.25
6 | Operation Curve tye | IEC NORMAL INV
7 | Type of reset curve | Immedietly
8 | Reset Delay time | 20 ms
9 | Minimum Operating time | 60 ms
10 | Allow non DIR | False
11 | Mesurment Mode | DFT
12 | Characterstic Angel | 90 DEG.
13 | Maximum Forword Angel | 80 DEG
14 | Maximum Reverse Angel | 80 DEG
15 | Maximum Operatonal Current | 0.005 * IN
16 | Minimum Operating Voltage | 0.01 un
17 | POL Reversal | False
18 | Voltage start value | 0.01 * UN
19 | Enable Voltage limit | True
20 | IO Signal se | Calculated IO
PHIPTOC1
1 | Operation | ON
2 | Number of start Phase | 1 Out of 3
3 | Start Value | 2.30 * IN
4 | Start Value multi | 1
5 | Operation Delay time | 310 ms
6 | Reset Delay time | 20 ms
DPHLPOC1
1 | Operation | on
2 | Number of start Phase | 1 Out of 3
3 | Start Value | 1.01 IN
4 | Start Value multi | 1
5 | Time Multiplier | 0.25
6 | Minimum Operate time | 20 MS
7 | Reset Delay time | 20 MS
8 | Operating Curve Time | IEC NORMAL INV
9 | Type of reset curve | Immedietly
10 | Mesurment Mode | DFT
11 | Directon Mode | Non Directional

## Breaker
Existing Setting
Sl. No. | Name |  |  |  | L |  |  | S |  | I |  |  | G |  | Remarks
| Breaker Name | Breaker Rating | Breaker Type | Breaker Make
|  | kA | -- |  | Pick-up (pu) | Time dial (s) | Characteristics | Pick-up (pu) | Time dial (s) | Pick-up (pu) | Time dial (s) | Characteristics | Pick-up (pu) | Time dial (s)
1 | HT Panel IC-1 | 11KV, 630A / Incomer Block-2 | 11 KV | ABB India Ltd. | [10 empty] | Trip time +,- 5%
2 | HT Panel IC-2 | 11KV, 630A / Incomer Block-3 | 11 KV | ABB India Ltd. | [10 empty] | Trip time +,- 5%
3 | HT Panel OG | 11KV,1250A / Outgoing | 11 KV | ABB India Ltd. | [10 empty] | Trip time +,- 5%
4 | HT Panel IC-4 | 11KV, 630A / Incomer Incomer MCR Inv 1&2 | 11 KV | ABB India Ltd. | [10 empty] | Trip time +,- 5%
5 | HT Panel IC-5 | 11KV, 630A / Incomer MCR Inv 3&4 | 11 KV | ABB India Ltd. | [10 empty] | Trip time +,- 5%
6 | HT Panel IC-1 | 11KV, 630A / Incomer Inv 1&4 | 11 KV | ABB India Ltd. | [10 empty] | Trip time +,- 5%
7 | HT Panel OG | 11KV, 630A / Outgoing | 11 KV | ABB India Ltd. | [10 empty] | Trip time +,- 5%
8 | HT Panel IC-2 | 11KV, 630A / Incomer Block-3 2&3 | 11 KV | ABB India Ltd. | [10 empty] | Trip time +,- 5%
9 | HT Panel IC-1 | 11KV, 630A / Incomer Inv 1&4 | 11 KV | ABB India Ltd. | [10 empty] | Trip time +,- 5%
10 | HT Panel OG | 11KV, 630A / Outgoing | 11 KV | ABB India Ltd. | [10 empty] | Trip time +,- 5%
11 | HT Panel IC-2 | 11KV, 630A / Incomer Block-3 2&3 | 11 KV | ABB India Ltd. | [10 empty] | Trip time +,- 5%

## CT & Relay
Existing Setting
Sl. No. | Name |  |  |  | 51 |  |  | 50 |  | 51N |  |  | 50N |  | Remarks
| Relay Name | CT Ratio |  | Relay Type | IDMT |  |  | DT |  | IDMT |  |  | DT
|  | Ir1 | Ir2 | -- | Pick-up (pu) | Time dial (s) | Characteristics | Pick-up (pu) | Time dial (s) | Pick-up (pu) | Time dial (s) | Characteristics | Pick-up (pu) | Time dial (s)
1 | REJ615 |  |  | Numeric Relay
2 | REJ601 |  |  | Numeric Relay
3 | REJ601 |  |  | Numeric Relay
4 | REJ601 |  |  | Numeric Relay
5 | REJ601 |  |  | Numeric Relay
6 | REJ601 |  |  | Numeric Relay
7 | REJ601 |  |  | Numeric Relay
8 | REJ601 |  |  | Numeric Relay
9 | REJ601 |  |  | Numeric Relay
10 | REJ601 |  |  | Numeric Relay
11 | REJ601 |  |  | Numeric Relay
12 | MCR CT | [13 empty] | 100/1
13 | BLOCK 2 CT | [13 empty] | 25/1
14 | BLOCK-3 CT | [13 empty] | 25/1