## Roaster-3 (hidden)
Roaster - 3 Plant
Department |  |  | Author |  | Status | [7 empty] | Date |  | Lang.
Power Consulting |  |  | Pritul Panchal |  | Rev A | [7 empty] | 2023-12-28 |  | en
sr. No | FeederType or Location | CT Ratio Amps | Relay Make | Relay Type | Relay NEMA Code | IEC Code | Prot Type | Relay Range |  | Exisitng Setting |  |  | Exisitng Setting |  |  | Remark
[8 empty] | Plug setting range | Time setting range (s) / TMs range | Plug setting | Time setting (s) / TMs | Charact eristic | Plug setting | Time setting (s) / TMs | Charact eristic
11kV CDSS S/s
1 | BUS-A_CDSS S/S SW-12 I/C | 750/1 | Siemens | SIPROTEC 7UM62 | 51 | I> | P/F | 0.10 .. 4.00 | 0.50 .. 15.00 | 3 | 0.05 | NI | 0.45 | 3.2 | EI |  | CT_ROASTER 3 (SEC-A) CDSS
[5 empty] | 50 | I>> | P/F Hs | 0.05 .. 20.00 | 0.00 .. 60.00 | 12 | 0.01 | DMT | 5 | 0.25 | DT
[5 empty] | 50-1 | I>>> | P/F Hs - 1 | 0.05 .. 20.00 | 0.00 .. 60.00 | 2.3 | 25 | DT
[5 empty] | 51N | I0> | EF | 0.10 .. 4.00 | 0.50 .. 15.00 | 0.6 | 20 | NI
[5 empty] | 50N | I0>> | E/F Hs | 0.05 .. 20.00 | 0.00 .. 60.00 | 0.01 | 0.01 | DMT | 0.34 | 0.25 | DT
2 | BUS-B_CDSS S/S SW-12 I/C | 750/1 | Siemens | SIPROTEC 7UM62 | 51 | I> | P/F | 0.10 .. 4.00 | 0.50 .. 15.00 | 3 | 0.05 | NI | 0.5 | 2.4 | EI |  | CT_O/G_ROASTER 3 (SECTION B) CDSS
[5 empty] | 50 | I>> | P/F Hs | 0.05 .. 20.00 | 0.00 .. 60.00 | 12 | 0.01 | DMT | 5 | 0.25 | DT
[5 empty] | 50-1 | I>>> | P/F Hs - 1 | 0.05 .. 20.00 | 0.00 .. 60.00 | 2.3 | 25 | DT
[5 empty] | 51N | I0> | EF | 0.10 .. 4.00 | 0.50 .. 15.00 | 0.6 | 20 | NI
[5 empty] | 50N | I0>> | E/F Hs | 0.05 .. 20.00 | 0.00 .. 60.00 | 0.01 | 0.01 | DMT | 0.4 | 0.25 | DT
3 | STG BUS I/C | 400/1 | ABB | SPAM150C | 50 | I>> | P/F Hs | 0.5...20.0 | 0.04...30 | 20 | 0.04 | DT |  |  |  |  | CT_STG
[5 empty] | 50N | I0> | E/F Hs | 1.0...100% | 0.05...30 | 1 | 0.05 | DT
|  |  | ABB | REF615 | 51 | I> | P/F | 0.05-0.01-5.00 | 0.025-0.005-15.000 |  |  |  | 1 | 0.42 | EI
[5 empty] | 50 | I>> | P/F Hs | 0.010-0.005-5.000 | 0.025-0.005-15.000 |  |  |  | 6.5 | 0.45 | DT
[5 empty] | 51N | I0> | EF | 0.1-0.01-40.00 | 40-10-200000 (ms)
[5 empty] | 50N | I0>> | E/F Hs | 0.1-0.01-40.00 | 40-10-200000 (ms) |  |  |  | 0.87 | 0.45 | DT
4 | O/G1 STG I/C | 600/1 |  |  | 51 | I> | P/F | [9 empty] | CT_O/G_1_STG 1
[5 empty] | 50 | I>> | P/F Hs
[5 empty] | 51N | I0> | EF
[5 empty] | 50N | I0>> | E/F Hs
|  |  | ABB | REF615 | 51 | I> | P/F | 0.05-0.01-5.00 | 0.025-0.005-15.000 |  |  |  | 0.59 | 0.35 | EI
[5 empty] | 50 | I>> | P/F Hs | 0.010-0.005-5.000 | 0.025-0.005-15.000 |  |  |  | 4.08 | 0.25 | DT
[5 empty] | 51N | I0> | EF | 0.1-0.01-40.00 | 40-10-200000 (ms)
[5 empty] | 50N | I0>> | E/F Hs | 0.1-0.01-40.00 | 40-10-200000 (ms) |  |  |  | 0.5 | 0.25 | DT
5 | I/C1 STG I/C | 700/1 | Siemens | 7SJ6001 | 51 | I> | P/F | 0.10 .. 4.00 | 0.05 .. 3.2 |  |  |  | 0.5 | 0.33 | EI |  | CT_O/G_1_STG 2
[5 empty] | 50 | I>> | P/F Hs | 0.10 .. 25 | 0.00 .. 60.00 |  |  |  | 3.5 | 0.25 | DT
[5 empty] | 50-1 | I>>> | P/F Hs - 1 | 0.3 .. 12.5
[5 empty] | 51N | I0> | EF | 0.05 .. 4.00 | 0.05 .. 3.2
[5 empty] | 50N | I0>> | E/F Hs | 0.05 .. 25 | 0.00 .. 60.00 |  |  |  | 0.4 | 0.25 | DT
6 | O/G2 STG I/C | 600/1 |  |  | 51 | I> | P/F | [9 empty] | CT_O/G_2_STG 1
[5 empty] | 50 | I>> | P/F Hs
[5 empty] | 51N | I0> | EF
[5 empty] | 50N | I0>> | E/F Hs
|  |  | ABB | REF615 | 51 | I> | P/F | 0.05-0.01-5.00 | 0.025-0.005-15.000 |  |  |  | 0.5 | 0.55 | EI
[5 empty] | 50 | I>> | P/F Hs | 0.010-0.005-5.000 | 0.025-0.005-15.000 |  |  |  | 4.09 | 0.25 | DT
[5 empty] | 51N | I0> | EF | 0.1-0.01-40.00 | 40-10-200000 (ms)
[5 empty] | 50N | I0>> | E/F Hs | 0.1-0.01-40.00 | 40-10-200000 (ms) |  |  |  | 0.5 | 0.25 | DT
7 | I/C2 STG I/C | 700/1 | Siemens | 7SJ6001 | 51 | I> | P/F | 0.10 .. 4.00 | 0.05 .. 3.2 |  |  |  | 0.3 | 1 | EI |  | CT_O/G_2_STG 2
[5 empty] | 50 | I>> | P/F Hs | 0.10 .. 25 | 0.00 .. 60.00 |  |  |  | 3.5 | 0.25 | DT
[5 empty] | 50-1 | I>>> | P/F Hs - 1 | 0.3 .. 12.5
[5 empty] | 51N | I0> | EF | 0.05 .. 4.00 | 0.05 .. 3.2
[5 empty] | 50N | I0>> | E/F Hs | 0.05 .. 25 | 0.00 .. 60.00 |  |  |  | 0.2 | 0.25 | DT
8 | O/G PFIC-11 | 200/1 | Siemens | 7SJ6001 | 51 | I> | P/F | 0.10 .. 4.00 | 0.05 .. 3.2 | 7 | 0.06 | NI | 0.8 | 0.1 | NI |  | CT_APFC-11
[5 empty] | 50 | I>> | P/F Hs | 0.10 .. 25 | 0.00 .. 60.00 | 1.6 | 1 | DMT | 25 | 0.05 | DT
[5 empty] | 50-1 | I>>> | P/F Hs - 1 | 0.3 .. 12.5 |  | 12.5 |  | DT
[5 empty] | 51N | I0> | EF | 0.05 .. 4.00 | 0.05 .. 3.2
[5 empty] | 50N | I0>> | E/F Hs | 0.05 .. 25 | 0.00 .. 60.00 | 0.05 |  | DT | 0.5 | 0.05 | DT
9 | O/G SO2 BLOWER | 250/1 | Siemens | SIPROTEC 7UM62 | 51 | I> | P/F | 0.10 .. 4.00 | 0.50 .. 15.00 | 4 | 0.2 | NI | 0.76 | 2 | NI |  | CT_SO2 BLOWER
[5 empty] | 50 | I>> | P/F Hs | 0.05 .. 20.00 | 0.00 .. 60.00 | 20 | 0.1 | DMT | 6.19 | 0.05 | DT
[5 empty] | 50N | I0>> | E/F Hs | 0.05 .. 25 | 0.00 .. 60.00 | 1 | 30 | NI | 0.5 | 0.05 | DT
10 | I/C TR-111-A | 130/1 | Siemens | 7SJ6001 | 51 | I> | P/F | 0.10 .. 4.00 | 0.05 .. 3.2 | 1 | 0.1 | NI | 1 | 1 | EI |  | CT_I/C_TR-111-A
[5 empty] | 50 | I>> | P/F Hs | 0.10 .. 25 | 0.00 .. 60.00 | 2.5 | 20 | DMT | 18.5 | 0.05 | DT
[5 empty] | 50-1 | I>>> | P/F Hs - 1 | 0.3 .. 12.5 |  | 12.5 |  | DT
[5 empty] | 51N | I0> | EF | 0.05 .. 4.00 | 0.05 .. 3.2 | 2.6 | 0.1 | NI
[5 empty] | 50N | I0>> | E/F Hs | 0.05 .. 25 | 0.00 .. 60.00 | 0.1 | 0.1 | DT | 0.5 | 0.05 | DT
11 | I/C TR-112-A | 130/1 | Siemens | 7SJ6001 | 51 | I> | P/F | 0.10 .. 4.00 | 0.05 .. 3.2 | 1 | 0.1 | NI | 1.1 | 1.7 | EI |  | CT_I/C_TR-112-A
[5 empty] | 50 | I>> | P/F Hs | 0.10 .. 25 | 0.00 .. 60.00 | 2.5 | 20 | DMT | 18.8 | 0.05 | DT
[5 empty] | 50-1 | I>>> | P/F Hs - 1 | 0.3 .. 12.5 |  | 12.5 |  | DT
[5 empty] | 51N | I0> | EF | 0.05 .. 4.00 | 0.05 .. 3.2 | 2.6 | 0.1 | NI
[5 empty] | 50N | I0>> | E/F Hs | 0.05 .. 25 | 0.00 .. 60.00 | 0.1 | 0.1 | DT | 0.5 | 0.05 | DT
12 | I/C TR-113-A | 130/1 | Siemens | 7SJ6001 | 51 | I> | P/F | 0.10 .. 4.00 | 0.05 .. 3.2 | 1 | 0.1 | NI | 1.1 | 2.2 | EI |  | CT_I/C_TR 113-A
[5 empty] | 50 | I>> | P/F Hs | 0.10 .. 25 | 0.00 .. 60.00 | 2.5 | 20 | DMT | 18.8 | 0.05 | DT
[5 empty] | 50-1 | I>>> | P/F Hs - 1 | 0.3 .. 12.5 |  | 12.5 |  | DT
[5 empty] | 51N | I0> | EF | 0.05 .. 4.00 | 0.05 .. 3.2 | 2.6 | 0.1 | NI
[5 empty] | 50N | I0>> | E/F Hs | 0.05 .. 25 | 0.00 .. 60.00 | 0.1 | 0.1 | DT | 0.5 | 0.05 | DT
13 | I/C TR 11-A | 150/1 | Siemens | 7SJ6001 | 51 | I> | P/F | 0.10 .. 4.00 | 0.05 .. 3.2 | 4 | 0.05 | NI | 1.1 | 1.2 | NI |  | CT_I/C_TR 11-A
[5 empty] | 50 | I>> | P/F Hs | 0.10 .. 25 | 0.00 .. 60.00 | 8 | 25 | DMT | 18.7 | 0.05 | DT
[5 empty] | 50N | I0>> | E/F Hs | 0.05 .. 25 | 0.00 .. 60.00 |  |  |  | 0.5 | 0.05 | DT
14 | I/C TR 11-B | 150/1 | Siemens | 7SJ6001 | 51 | I> | P/F | 0.10 .. 4.00 | 0.05 .. 3.2 | 4 | 0.05 | NI | 1.1 | 1.1 | NI |  | CT_I/C_TR 11-B
[5 empty] | 50 | I>> | P/F Hs | 0.10 .. 25 | 0.00 .. 60.00 | 8 | 25 | DMT | 18.7 | 0.05 | DT
[5 empty] | 50N | I0>> | E/F Hs | 0.05 .. 25 | 0.00 .. 60.00 |  |  |  | 0.5 | 0.05 | DT
15 | O/G PFIC-12 | 200/1 | Siemens | 7SJ6001 | 51 | I> | P/F | 0.10 .. 4.00 | 0.05 .. 3.2 | 7 | 0.06 | NI | 1.5 | 0.1 | NI |  | CT_PFIC-12
[5 empty] | 50 | I>> | P/F Hs | 0.10 .. 25 | 0.00 .. 60.00 | 1.6 | 1 | DMT | 25 | 0.05 | DT
[5 empty] | 50-1 | I>>> | P/F Hs - 1 | 0.3 .. 12.5 |  | 12.5 |  | DT
[5 empty] | 51N | I0> | EF | 0.05 .. 4.00 | 0.05 .. 3.2
[5 empty] | 50N | I0>> | E/F Hs | 0.05 .. 25 | 0.00 .. 60.00 | 0.05 |  | DT | 0.5 | 0.05 | DT
16 | I/C TR 113-B | 130/1 | Siemens | 7SJ6001 | 51 | I> | P/F | 0.10 .. 4.00 | 0.05 .. 3.2 | 1 | 0.1 | NI | 1.1 | 2.3 | EI |  | CT_I/C_TR 113-B
[5 empty] | 50 | I>> | P/F Hs | 0.10 .. 25 | 0.00 .. 60.00 | 2.5 | 20 | DMT | 18.5 | 0.05 | DT
[5 empty] | 50-1 | I>>> | P/F Hs - 1 | 0.3 .. 12.5 |  | 12.5 |  | DT
[5 empty] | 51N | I0> | EF | 0.05 .. 4.00 | 0.05 .. 3.2 | 2.6 | 0.1 | NI
[5 empty] | 50N | I0>> | E/F Hs | 0.05 .. 25 | 0.00 .. 60.00 | 0.1 | 0.1 | DT | 0.5 | 0.05 | DT
17 | I/C TR-112-B | 130/1 | Siemens | 7SJ6001 | 51 | I> | P/F | 0.10 .. 4.00 | 0.05 .. 3.2 | 1 | 0.1 | NI | 1 | 1.1 | EI |  | CT_I/C_TR-112-B
[5 empty] | 50 | I>> | P/F Hs | 0.10 .. 25 | 0.00 .. 60.00 | 2.5 | 20 | DMT | 17.5 | 0.05 | DT
[5 empty] | 50-1 | I>>> | P/F Hs - 1 | 0.3 .. 12.5 |  | 12.5 |  | DT
[5 empty] | 51N | I0> | EF | 0.05 .. 4.00 | 0.05 .. 3.2 | 2.6 | 0.1 | NI
[5 empty] | 50N | I0>> | E/F Hs | 0.05 .. 25 | 0.00 .. 60.00 | 0.1 | 0.1 | DT | 0.5 | 0.05 | DT
18 | I/C TR 111-B | 130/1 | Siemens | 7SJ6001 | 51 | I> | P/F | 0.10 .. 4.00 | 0.05 .. 3.2 | 1 | 0.1 | NI | 1 | 1.1 | EI |  | CT_I/C_TR 111-B
[5 empty] | 50 | I>> | P/F Hs | 0.10 .. 25 | 0.00 .. 60.00 | 2.5 | 20 | DMT | 18.8 | 0.05 | DT
[5 empty] | 50-1 | I>>> | P/F Hs - 1 | 0.3 .. 12.5 |  | 12.5 |  | DT
[5 empty] | 51N | I0> | EF | 0.05 .. 4.00 | 0.05 .. 3.2 | 2.6 | 0.1 | NI
[5 empty] | 50N | I0>> | E/F Hs | 0.05 .. 25 | 0.00 .. 60.00 | 0.1 | 0.1 | DT | 0.5 | 0.05 | DT
19 | O/G ROASTER AIR BLOWER | 120/1 | Siemens | 7SJ6001 | 51 | I> | P/F | 0.10 .. 4.00 | 0.05 .. 3.2 | 2.9 | 0.2 | NI | 0.7 | 2 | NI |  | CT_ROASTER AIR BLOWER
[5 empty] | 50 | I>> | P/F Hs | 0.10 .. 25 | 0.00 .. 60.00 | 0.7 | 31 | DMT | 5.5 | 0.05 | DT
[5 empty] | 50-1 | I>>> | P/F Hs - 1 | 0.3 .. 12.5 |  | 7 |  | DT
[5 empty] | 51N | I0> | EF | 0.05 .. 4.00 | 0.05 .. 3.2 | Disabled |  |  | Disabled
[5 empty] | 50N | I0>> | E/F Hs | 0.05 .. 25 | 0.00 .. 60.00 |  |  |  | 2.5 | 0.05 | DT
20 | O/G RO-ZLD TR | 250/5 |  |  | 51 | I> | P/F | [9 empty] | CT_I/C_RO-ZLD TR 1
[5 empty] | 50 | I>> | P/F Hs
[5 empty] | 51N | I0> | EF
[5 empty] | 50N | I0>> | E/F Hs
21 | I/C RO-ZLD TR | 250/5 |  |  | 51 | I> | P/F | [9 empty] | CT_I/C_RO-ZLD TR 2
[5 empty] | 50 | I>> | P/F Hs
[5 empty] | 51N | I0> | EF
[5 empty] | 50N | I0>> | E/F Hs
3.3kV CDSS S/s
20 | I/C TR 11-A | 500/1 | Siemens | 7SJ6001 | 51 | I> | P/F | 0.1-0.1-4 | 0.050-0.010-3.200 | 4 | 0.05 | NI | 0.2 | 1.95 | NI |  | CT_O/G_TR 11-A
[5 empty] | 50 | I>> | P/F Hs | 0.100-0.100-25.0 | 0.010-0.010-60.0 |  |  |  | 5 | 0.25 | DT
[5 empty] | 51N | I0> | EF | 0.05-0.01-4 | 0.050-0.010-3.200 | 8 | 25 | DMT
[5 empty] | 50N | I0>> | EF Hs | 0.050-0.0100-25.0 | 0.01-0.01-60 | Not Available |  |  | 0.5 | 0.25 | DT
21 | I/C TR 11-B | 500/1 | Siemens | 7SJ6001 | 51 | I> | P/F | 0.1-0.1-4 | 0.050-0.010-3.200 | 4 | 0.05 | NI | 0.3 | 1.6 | NI |  | CT_O/G_TR 11-B
[5 empty] | 50 | I>> | P/F Hs | 0.100-0.100-25.0 | 0.010-0.010-60.0 |  |  |  | 5 | 0.25 | DT
[5 empty] | 51N | I0> | EF | 0.05-0.01-4 | 0.050-0.010-3.200 | 8 | 25 | DMT
[5 empty] | 50N | I0>> | EF Hs | 0.050-0.0100-25.0 | 0.01-0.01-60 | Not Available |  |  | 0.5 | 0.25 | DT
22 | O/G BALL MILL1 | 65/1 | Siemens | 7SJ6001 | 51 | I> | P/F | 0.1-0.1-4 | 0.050-0.010-3.200 | 4 | 0.2 | NI | 1.1 | 2 | NI |  | CT_BALL MILL1
[5 empty] | 50 | I>> | P/F Hs | 0.100-0.100-25.0 | 0.010-0.010-60.0 | 1.1 | 40 | DMT | 8.6 | 0.05 | DT
[5 empty] | 51N | I0> | EF | 0.05-0.01-4 | 0.050-0.010-3.200
[5 empty] | 50N | I0>> | EF Hs | 0.050-0.0100-25.0 | 0.01-0.01-60 | Not Available |  |  | 0.5 | 0.05 | DT
23 | O/G CIRCULATING PUMP WHRB | 65/1 | Siemens | 7SJ6001 | 51 | I> | P/F | 0.1-0.1-4 | 0.050-0.010-3.200 | 4 | 0.05 | NI | 0.8 | 2 | NI |  | CT_CIRCULATING PUMP WHRB
[5 empty] | 50 | I>> | P/F Hs | 0.100-0.100-25.0 | 0.010-0.010-60.0 | 0.9 | 35 | DMT | 6.7 | 0.05 | DT
[5 empty] | 51N | I0> | EF | 0.05-0.01-4 | 0.050-0.010-3.200 | 12.5
[5 empty] | 50N | I0>> | EF Hs | 0.050-0.0100-25.0 | 0.01-0.01-60 | Not Available |  |  | 0.5 | 0.05 | DT
24 | O/G FEED WATER PUMP | 65/1 | Siemens | 7SJ6001 | 51 | I> | P/F | 0.1-0.1-4 | 0.050-0.010-3.200 | 4 | 0.05 | NI | 0.9 | 2 | NI |  | CT_FEED WATER PUMP
[5 empty] | 50 | I>> | P/F Hs | 0.100-0.100-25.0 | 0.010-0.010-60.0 | 0.9 | 35 | DMT | 7.4 | 0.05 | DT
[5 empty] | 51N | I0> | EF | 0.05-0.01-4 | 0.050-0.010-3.200 | 12.5
[5 empty] | 50N | I0>> | EF Hs | 0.050-0.0100-25.0 | 0.01-0.01-60 | Not Available |  |  | 0.5 | 0.05 | DT
0.415kV RO ZLD PCC
25 | I/C RO-ZLD PCC | 5000A rating | Siemens | ETU45B | L |  | O/L | 0.4-0.45-0.5-0.55-0.6-0.65-0.7-0.8-0.9-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 0.8 | 10 |  | 0.6 | 2 |  |  | CB_RO-ZLD TR
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 | 3 | 4 |  | 3 | 400
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20 | 6
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | 400 | 0.5 |  | 300 | 200
26 | O/G COMPRESSOR MOTOR | 100A rating | Siemens | MCCB | L |  | O/L | 1 | 1 | 1 | 2 |  | 1 | 1 |  |  | CB_O/G2_MCC-118 2
[5 empty] | I |  | Instantaneous | 1 | 0.01 | 900 | 0.1 |  | 1 | 0.01
27 | O/G MCC-1 | 1250A rating | Siemens | ETU45B | L |  | O/L | 0.4-0.45-0.5-0.55-0.6-0.65-0.7-0.8-0.9-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 1 | 1 |  | 0.8 | 2 |  |  | CB_MCC-1 1
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 | 3 | 4 |  | 4 | 200
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20 | 3
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | Disabled |  |  | 600 | 200
28 | I/C MCC-1 | 800A rating | Siemens | ETU437W | L |  | O/L | 0.4-0.45-0.5-0.55-0.6-0.65-0.7-0.8-0.9-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 0.4 | 10 |  | 1 | 2 |  |  | CB_MCC-1 2
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 | 1.25 | 0.02 |  | 4 | 200
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20 | 20
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | 300 | 0.1 |  | 600 | 200
29 | O/G MCC-2 | 1250A rating | Siemens | ETU45B | L |  | O/L | 0.4-0.45-0.5-0.55-0.6-0.65-0.7-0.8-0.9-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 1 | 10 |  | 0.8 | 2 |  |  | CB_MCC-2 1
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 | 3 | 4 |  | 4 | 200
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20 | 3
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | Disabled |  |  | 600 | 200
30 | I/C MCC-2 | 800A rating | Siemens | ETU37WT | L |  | O/L | 0.4-0.45-0.5-0.55-0.6-0.65-0.7-0.8-0.9-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 1 | 10 |  | 1 | 2 |  |  | CB_MCC-2 2
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 | 1.25 | 0.2 |  | 4 | 200
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20 | 20
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | 100 | 0.2 |  | 600 | 200
31 | O/G VFD-1 | 630A rating | Siemens | ETU45B | L |  | O/L | 0.4-0.45-0.5-0.55-0.6-0.65-0.7-0.8-0.9-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 1 | 10 |  | 0.45 | 2 |  |  | CB_VFD-2
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 | 3 | 4 |  | 4 | M
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20 | 3
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | Disabled |  |  | 600 | 100
32 | O/G VFD-2 | 1250A rating | Siemens | ETU45B | L |  | O/L | 0.4-0.45-0.5-0.55-0.6-0.65-0.7-0.8-0.9-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 1 | 10 |  | 0.9 | 2 |  |  | CB_VFD-1
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 | 3 | 4 |  | 8 | M
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20 | 3
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | Disabled |  |  | 600 | 100
33 | O/G CAP BUS | 2000A rating | Siemens | ETU45B | L |  | O/L | 0.4-0.45-0.5-0.55-0.6-0.65-0.7-0.8-0.9-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 1 | 10 |  | 0.5 | 2 |  |  | CB_CAP BUS
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 | 3 | 4 |  | 3 | 200
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20 | 3
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | Disabled |  |  | 600 | 200
34 | O/G PIROTEC PCC (From RO-ZLD PCC) | 800A rating | Schneider | MVS20N ETA 6G | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.9-0.95-0.98-1 | 0.5-1-2-4-8-12-16-20-24 | 0.4 | 0.5 |  | 0.5 | 2 |  |  | CB2_O/G2_PYROTEC PCC
[5 empty] | S |  | S/C | 1.5-2-2.5-3-4-5-6-8-10 | 0-0.1-0.2-0.3-0.4 (ms) | 1.5 | 0.1 |  | 4 | 0.2
[5 empty] | I |  | Instantaneous | 2-3-4-6-8-10-12-15 | 0.025 | 2
[5 empty] | G |  | Ground | 500-640-720-800-880-960-1040-1120-1200 | 0-0.1-0.2-0.3-0.4 (ms) | 500 | 0.1 |  | 600 | 0.2
0.415kV PCC - 113
35 | I/C PCC-113_BUS A | 4000A rating | Siemens | ETU45B | L |  | O/L | 0.4-0.45-0.5-0.55-0.6-0.65-0.7-0.8-0.9-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 1 | 21 |  | 1 | 2 |  |  | CB_TR 113-A
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 | 10 | 0.4 |  | 2 | 400
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20 | 10
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | 1200 | 0.2 |  | 900 | 400
36 | I/C PCC-113_BUS B | 4000A rating | Siemens | ETU45B | L |  | O/L | 0.4-0.45-0.5-0.55-0.6-0.65-0.7-0.8-0.9-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 1 | 21 |  | 1 | 2 |  |  | CB_TR 113-B
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 | 10 | 0.4 |  | 2 | 400
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20 | 10
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | 1200 | 0.2 |  | 900 | 400
37 | O/G GA-55 | 1000A rating | Siemens | ETU45B | L |  | O/L | 0.4-0.45-0.5-0.55-0.6-0.65-0.7-0.8-0.9-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 0.4 | 2 |  | 0.4 | 2 |  |  | CB_GA-55
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 | 1.25 | 0.1
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20 | 12 |  |  | 1.5 | 20
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | 100 | 0.1 |  | 600 | 100
38 | O/G MCC 115 BUS B I/C-2 | 1000A rating | Siemens | ETU45B | L |  | O/L | 0.4-0.45-0.5-0.55-0.6-0.65-0.7-0.8-0.9-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 0.8 | 3.5 |  | 0.9 | 3.5 |  |  | CB_I/C2_MCC 115 1
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 | 1 | 0.2 |  | 8 | 200
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20 | 8
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | 900 | 0.1 |  | 600 | 200
39 | I/C MCC 115 BUS B I/C-2 | 800A rating | Siemens | ETU45B | L |  | O/L | 0.4-0.45-0.5-0.55-0.6-0.65-0.7-0.8-0.9-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 0.9 | 3.5 |  | 0.9 | 3.5 |  |  | CB_I/C2_MCC 115 2
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 | Not Available
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20 | Not Available
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | 900 | 0.1
40 | O/G MCC 114 BUS B I/C-2 | 1000A rating | Siemens | ETU45B | L |  | O/L | 0.4-0.45-0.5-0.55-0.6-0.65-0.7-0.8-0.9-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 1 | 2 |  | 0.8 | 2 |  |  | CB_O/G2_MCC-114_BUS B 1
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 | 12 | 0.2 |  | 8 | 200
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20 | 8
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | 900 | 0.1 |  | 600 | 200
41 | I/C MCC 114 BUS B I/C-2 | 1000A rating | Siemens | ETU45B | L |  | O/L | 0.4-0.45-0.5-0.55-0.6-0.65-0.7-0.8-0.9-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 0.8 | 0.1 |  | 0.8 | 2 |  |  | CB_O/G2_MCC-114_BUS B 2
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 | 12 |  |  | 8 | 200
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20 | Not Available
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | Disabled |  |  | 600 | 200
42 | O/G PDB 112 BUS B I/C-2 | 1000A rating | Siemens | ETU45B | L |  | O/L | 0.4-0.45-0.5-0.55-0.6-0.65-0.7-0.8-0.9-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 0.8 | 3.5 |  | 0.8 | 3.5 |  |  | CB_O/G2_PDB-112_BUS B 1
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 | 12 | 0.4 |  | 8 | 200
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20 | 12
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | 1200 | 0.2 |  | 600 | 200
43 | I/C PDB 112 BUS B I/C-2 | 1000A rating | Siemens | ETU45B | L |  | O/L | 0.4-0.45-0.5-0.55-0.6-0.65-0.7-0.8-0.9-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 0.8 | 3.5 |  | 0.8 | 3.5 |  |  | CB_O/G2_PDB-112_BUS B 2
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 | 12 | 0.4 |  | 8 | 200
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20 | 12
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | 1200 | 0.2 |  | 600 | 200
44 | O/G COOLING MOTOR 2 FOR TOWER4 | 400/1 | ABB | SPAM150C | 51 | I> | P/F | 0.5-0.01-2.5 | 0.05-0.01-1.0 | 20 | 0.04 | DT | 0.9 | 1 | NI |  | CT_COOLING MOTOR 2 FOR TOWER4
[5 empty] | 50 | I>> | P/F Hs | 0.500-0.010-40.0 | 0.040-0.010-300.0 |  |  |  | 7.32 | 0.05 | DT
[5 empty] | 51N | I0> | E/F | 0.100-0.010-1.00 | 0.050-0.010-30 |  |  |  | 0.2 | 1 | NI
[5 empty] | 50N | I0>> | E/F Hs | 0.100-0.010-10.0 | 0.050-0.010-300.0 | 1 | 0.05 | DT | 0.5 | 0.05 | DT
45 | O/G COOLING MOTOR 4 FOR TOWER1 | 400/1 | ABB | SPAM150C | 51 | I> | P/F | 0.5-0.01-2.5 | 0.05-0.01-1.0 | 20 | 0.04 | DT | 0.5 | 1 | NI |  | CT_COOLING MOTOR 4 FOR TOWER1
[5 empty] | 50 | I>> | P/F Hs | 0.500-0.010-40.0 | 0.040-0.010-300.0 |  |  |  | 2.03 | 0.05 | DT
[5 empty] | 51N | I0> | E/F | 0.100-0.010-1.00 | 0.050-0.010-30 |  |  |  | 0.2 | 1 | NI
[5 empty] | 50N | I0>> | E/F Hs | 0.100-0.010-10.0 | 0.050-0.010-300.0 | 1 | 0.05 | DT | 0.5 | 0.05 | DT
46 | O/G IR-3 | 630A rating | Siemens | ETU45B | L |  | O/L | 0.4-0.45-0.5-0.55-0.6-0.65-0.7-0.8-0.9-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 0.8 | 0.1 |  | 0.45 | 2 |  |  | CB_IR-3
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 | Not Available |  |  | 4 | 200
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20 | Not Available
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | Disabled |  |  | 300 | 200
46 | O/G MCC 118 BUS B I/C-2 | 1000A rating | Siemens | ETU45B | L |  | O/L | 0.4-0.45-0.5-0.55-0.6-0.65-0.7-0.8-0.9-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 1 | 2 |  | 1 | 2 |  |  | CB_O/G2_MCC-118 1
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 | 12 | 0.4 |  | 8 | 200
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20 | 8
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | 900 | 0.1 |  | 600 | 200
47 | I/C MCC 118 BUS B I/C-2 | 630A rating | Siemens | MCCB | L |  | O/L | 0.8-0.1-1.0 | 1 | 1 | 2 |  | 1 | 1 |  |  | CB_O/G2_MCC-118 2
[5 empty] | I |  | Instantaneous | 5-1-10 | 0.01 | 900 | 0.1 |  | 10 | 0.01
48 | O/G COOLING WATER PUMP 3 FOR TOWER 2 | 400/1 | ABB | SPAM150C | 51 | I> | P/F | 0.5-0.01-2.5 | 0.05-0.01-1.0 | 20 | 0.04 | DT | 0.9 | 1 | NI |  | CT_COOLING WATER PUMP 3 FOR TOWER 2
[5 empty] | 50 | I>> | P/F Hs | 0.500-0.010-40.0 | 0.040-0.010-300.0 |  |  |  | 7.32 | 0.05 | DT
[5 empty] | 51N | I0> | E/F | 0.100-0.010-1.00 | 0.050-0.010-30 |  |  |  | 0.2 | 1 | NI
[5 empty] | 50N | I0>> | E/F Hs | 0.100-0.010-10.0 | 0.050-0.010-300.0 | 1 | 0.05 | DT | 0.5 | 0.05 | DT
49 | O/G COOLING WATER PUMP 2 FOR TOWER 5 | 400/1 | ABB | SPAM150C | 51 | I> | P/F | 0.5-0.01-2.5 | 0.05-0.01-1.0 | 20 | 0.04 | DT | 0.9 | 1 | NI |  | CT_COOLING WATER PUMP 2 FOR TOWER 5
[5 empty] | 50 | I>> | P/F Hs | 0.500-0.010-40.0 | 0.040-0.010-300.0 |  |  |  | 7.32 | 0.05 | DT
[5 empty] | 51N | I0> | E/F | 0.100-0.010-1.00 | 0.050-0.010-30 |  |  |  | 0.2 | 1 | NI
[5 empty] | 50N | I0>> | E/F Hs | 0.100-0.010-10.0 | 0.050-0.010-300.0 | 1 | 0.05 | DT | 0.5 | 0.05 | DT
50 | O/G IR COMP 5 | 400/1 | ABB | SPAM150C | 51 | I> | P/F | 0.5-0.01-2.5 | 0.05-0.01-1.0 | 20 | 0.04 | DT | 0.72 | 1 | NI |  | CT_IR COMP 5
[5 empty] | 50 | I>> | P/F Hs | 0.500-0.010-40.0 | 0.040-0.010-300.0 |  |  |  | 5.88 | 0.05 | DT
[5 empty] | 51N | I0> | E/F | 0.100-0.010-1.00 | 0.050-0.010-30 |  |  |  | 0.2 | 1 | NI
[5 empty] | 50N | I0>> | E/F Hs | 0.100-0.010-10.0 | 0.050-0.010-300.0 | 1 | 0.05 | DT | 0.5 | 0.05 | DT
51 | O/G COOLING AIR FAN | 630A rating | Siemens | ETU45B | L |  | O/L | 0.4-0.45-0.5-0.55-0.6-0.65-0.7-0.8-0.9-1 | 2-3.5-5.5-8-10-14-17-21-25-30 |  |  |  | 0.4 | 2 |  |  | CB_O/G_COOLING AIR FAN 45KW
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 |  |  |  | 1.25 | M
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 |  |  |  | 300 | 100
52 | O/G MCC 111 BUS B I/C-2 | 1000A rating | Siemens | ETU45B | L |  | O/L | 0.4-0.45-0.5-0.55-0.6-0.65-0.7-0.8-0.9-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 0.8 | 3.5 |  | 0.8 | 3.5 |  |  | CB_O/G2_MCC 111 1
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 | 12 | 0.3 |  | 2 | 200
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20 | 12
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | 1200 | 0.2 |  | 600 | 200
53 | I/C MCC 111 BUS B I/C-2 | 800A rating | Siemens | ETU45B | L |  | O/L | 0.4-0.45-0.5-0.55-0.6-0.65-0.7-0.8-0.9-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 1 |  |  | 1 | 2 |  |  | CB_O/G2_MCC 111 2
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 | 9 | 0.2 |  | 2.5 | 200
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20 | 12
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | 900 | 0.2 |  | 600 | 200
54 | O/G COOLING WATER PUMP 1 FOR TOWER 1 | 400/1 | ABB | SPAM150C | 51 | I> | P/F | 0.5-0.01-2.5 | 0.05-0.01-1.0 | 20 | 0.04 | DT | 0.9 | 1 | NI |  | CT_COOLING WATER PUMP 1 FOR TOWER 1
[5 empty] | 50 | I>> | P/F Hs | 0.500-0.010-40.0 | 0.040-0.010-300.0 |  |  |  | 7.32 | 0.05 | DT
[5 empty] | 51N | I0> | E/F | 0.100-0.010-1.00 | 0.050-0.010-30 |  |  |  | 0.2 | 1 | NI
[5 empty] | 50N | I0>> | E/F Hs | 0.100-0.010-10.0 | 0.050-0.010-300.0 | 1 | 0.05 | DT | 0.5 | 0.05 | DT
55 | O/G WGP-2 TR | 630A rating | Siemens | ETU45B | L |  | O/L | 0.4-0.45-0.5-0.55-0.6-0.65-0.7-0.8-0.9-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 1 | 2 |  | 0.8 | 2 |  |  | CB_O/G_WGP-2 TR 1
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 | 12 | 0.2 |  | 4 | 200
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20 | 8
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | 900 | 0.1 |  | 600 | 200
56 | I/C WGP-2 TR | 400A rating | Siemens | MCCB | L |  | O/L | 0.8-0.1-1.0 | 1 | 1 | 2 |  | 1 | 1 |  |  | CB_O/G_WGP-2 TR 2
[5 empty] | I |  | Instantaneous | 5-1-10 | 0.01 | 900 | 0.1 |  | 5 | 0.01
57 | O/G FILTER WATER MCC PH-1 I/C-2 | 1000A rating | Siemens | ETU45B | L |  | O/L | 0.4-0.45-0.5-0.55-0.6-0.65-0.7-0.8-0.9-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 1 | 2 |  | 1 | 2 |  |  | CB_O/G2_FILTER WATER MCC PH-1 1
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 | 12 | 0.2 |  | 8 | 200
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20 | 8
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | 900 | 0.1 |  | 600 | 200
58 | I/C FILTER WATER MCC PH-1 I/C-2 | 400A rating | Siemens | MCCB | L |  | O/L | 0.8-0.1-1.0 | 1 | 1 | 2 |  | 1 | 1 |  |  | CB_O/G2_FILTER WATER MCC PH-1 2
[5 empty] | I |  | Instantaneous | 5-1-10 | 0.01 | 900 | 0.1 |  | 5 | 0.01
0.415kV PCC - 112
59 | I/C PCC-112_BUS A | 4000A rating | Siemens | ETU45B | L |  | O/L | 0.4-0.45-0.5-0.55-0.6-0.65-0.7-0.8-0.9-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 1 | 21 |  | 0.8 | 2 |  |  | CB_TR-112-A
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 | 10 | 0.4 |  | 2 | 400
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20 | 10
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | 1200 | 0.2 |  | 600 | 400
60 | I/C PCC-112_BUS B | 4000A rating | Siemens | ETU45B | L |  | O/L | 0.4-0.45-0.5-0.55-0.6-0.65-0.7-0.8-0.9-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 1 | 21 |  | 0.5 | 2 |  |  | CB_TR-112-B
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 | 10 | 0.4 |  | 6 | 400
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20 | 10
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | 1200 | 0.2 |  | 600 | 400
61 | O/G WGP-3 TR | 630A rating | Siemens | ETU45B | L |  | O/L | 0.4-0.45-0.5-0.55-0.6-0.65-0.7-0.8-0.9-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 0.8 | 2 |  | 0.8 | 2 |  |  | CB_I/C_WGP-3 TR 1
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 | 12 | 0.2
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20 | 8 |  |  | 6 | 20
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | 900 | 0.1 |  | 600 | 200
62 | I/C WGP-3 TR | 400A rating | Siemens | MCCB | L |  | O/L | 0.8-0.1-1.0 | 1 | 1 | 2 |  | 1 | 1 |  |  | CB_I/C_WGP-3 TR 2
[5 empty] | I |  | Instantaneous | 5-1-10 | 0.01 | 900 | 0.1 |  | 5 | 0.01
63 | O/G WGP-4 TR | 630A rating | Siemens | ETU45B | L |  | O/L | 0.4-0.45-0.5-0.55-0.6-0.65-0.7-0.8-0.9-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 0.8 | 2 |  | 0.8 | 2 |  |  | CB_I/C_WGP-4 TR 1
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 | 12 | 0.2
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20 | 8 |  |  | 3 | 20
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | 900 | 0.1 |  | 600 | 200
64 | I/C WGP-4 TR | 400A rating | Siemens | MCCB | L |  | O/L | 0.8-0.1-1.0 | 1 | 1 | 2 |  | 1 | 1 |  |  | CB_I/C_WGP-4 TR 2
[5 empty] | I |  | Instantaneous | 5-1-10 | 0.01 | 900 | 0.1 |  | 5 | 0.01
65 | O/G WGP-1 TR | 630A rating | Siemens | ETU45B | L |  | O/L | 0.4-0.45-0.5-0.55-0.6-0.65-0.7-0.8-0.9-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 0.8 | 2 |  | 1 | 2 |  |  | CB_I/C_WGP-1 TR 1
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 | 12 | 0.2
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20 | 8 |  |  | 3 | 20
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | 900 | 0.1 |  | 600 | 200
66 | I/C WGP-1 TR | 400A rating | Siemens | MCCB | L |  | O/L | 0.8-0.1-1.0 | 1 | 1 | 2 |  | 1 | 1 |  |  | CB_I/C_WGP-1 TR 2
[5 empty] | I |  | Instantaneous | 5-1-10 | 0.01 | 900 | 0.1 |  | 5 | 0.01
67 | O/G SCREW COMPRESSOR PNEUMATIC-3 | 400/1 | ABB | SPAM150C | 51 | I> | P/F | 0.5-0.01-2.5 | 0.05-0.01-1.0 | 20 | 0.04 | DT | 0.72 | 1 | NI |  | CT_O/G_SCREW COMPRESSOR PNEUMATIC-3
[5 empty] | 50 | I>> | P/F Hs | 0.500-0.010-40.0 | 0.040-0.010-300.0 |  |  |  | 5.85 | 0.05 | DT
[5 empty] | 51N | I0> | E/F | 0.100-0.010-1.00 | 0.050-0.010-30 |  |  |  | 0.3 | 1 | NI
[5 empty] | 50N | I0>> | E/F Hs | 0.100-0.010-10.0 | 0.050-0.010-300.0 | 1 | 0.05 | DT | 0.5 | 0.05 | DT
68 | O/G COOLING WATER PUMP 1 FOR TOWER 2 | 400/1 | ABB | SPAM150C | 51 | I> | P/F | 0.5-0.01-2.5 | 0.05-0.01-1.0 | 20 | 0.04 | DT | 0.9 | 1 | NI |  | CT_O/G_COOLING WATER PUMP 1 FOR TOWER 2
[5 empty] | 50 | I>> | P/F Hs | 0.500-0.010-40.0 | 0.040-0.010-300.0 |  |  |  | 7.32 | 0.05 | DT
[5 empty] | 51N | I0> | E/F | 0.100-0.010-1.00 | 0.050-0.010-30 |  |  |  | 0.2 | 1 | NI
[5 empty] | 50N | I0>> | E/F Hs | 0.100-0.010-10.0 | 0.050-0.010-300.0 | 1 | 0.05 | DT | 0.5 | 0.05 | DT
69 | O/G COOLING WATER PUMP 3 FOR TOWER 1 | 400/1 | ABB | SPAM150C | 51 | I> | P/F | 0.5-0.01-2.5 | 0.05-0.01-1.0 | 20 | 0.04 | DT | 0.9 | 1 | NI |  | CT_O/G_COOLING WATER PUMP 3 FOR TOWER 1
[5 empty] | 50 | I>> | P/F Hs | 0.500-0.010-40.0 | 0.040-0.010-300.0 |  |  |  | 7.32 | 0.05 | DT
[5 empty] | 51N | I0> | E/F | 0.100-0.010-1.00 | 0.050-0.010-30 |  |  |  | 0.2 | 1 | NI
[5 empty] | 50N | I0>> | E/F Hs | 0.100-0.010-10.0 | 0.050-0.010-300.0 | 1 | 0.05 | DT | 0.5 | 0.05 | DT
70 | O/G MCC-116 BUS A I/C-1 | 1000A rating | Siemens | ETU45B | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.9-0.95-0.98-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 0.8 | 3.5 |  | 0.8 | 3.5 |  |  | CB_O/G1_MCC-116_BUS A 1
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 | 12 | 0.4 |  | 6 | 200
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20 | 12
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | 900 | 0.2 |  | 600 | 200
71 | I/C MCC-116 BUS A I/C-1 | 1000A rating | Schneider | MicroLogic 6.0 | L |  | O/L | 0.4-0.45-0.5-0.55-0.6-0.65-0.7-0.8-0.9-1 | 0.5-1-2-4-8-12-16-20-24 | 0.9 | 2 |  | 0.9 | 2 |  |  | CB_O/G1_MCC-116_BUS A 2
[5 empty] | S |  | S/C | 1.5-2-2.5-3-4-5-6-8-10 | 0.1-0.2-0.3-0.4 | Not Available
[5 empty] | I |  | Instantaneous | 2-3-4-6-8-10-12-15 | 50 | Not Available
[5 empty] | G |  | Ground | 0.2-0.3-0.4-0.5-0.6-0.7-0.8-0.9-1.0 | 0.1-0.2-0.3-0.4 | Not Available
72 | O/G MCC 113 BUS B I/C-2 | 1000A rating | Siemens | ETU45B | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.9-0.95-0.98-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 0.8 | 2 |  | 0.8 | 2 |  |  | CB_O/G2_MCC 113 1
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 | 12 | 0.2 |  | 3 | 200
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20 | 8
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | 900 | 0.2 |  | 600 | 200
73 | I/C MCC 113 BUS B I/C-2 | 1000A rating | Siemens | ETU45B | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.9-0.95-0.98-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 0.8 | 2 |  | 0.8 | 2 |  |  | CB_O/G2_MCC 113 2
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 | 12 | 0.2 |  | 3 | 200
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20 | 8
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | 900 | 0.2 |  | 900 | 200
74 | O/G COOLING WATER PUMP 1 FOR TOWER 4 | 400/1 | ABB | SPAM150C | 51 | I> | P/F | 0.5-0.01-2.5 | 0.05-0.01-1.0 | 20 | 0.04 | DT | 0.9 | 1 | NI |  | CT_COOLING WATER PUMP 1 FOR TOWER 4
[5 empty] | 50 | I>> | P/F Hs | 0.500-0.010-40.0 | 0.040-0.010-300.0 |  |  |  | 7.32 | 0.05 | DT
[5 empty] | 51N | I0> | E/F | 0.100-0.010-1.00 | 0.050-0.010-30 |  |  |  | 0.2 | 1 | NI
[5 empty] | 50N | I0>> | E/F Hs | 0.100-0.010-10.0 | 0.050-0.010-300.0 | 1 | 0.05 | DT | 0.5 | 0.05 | DT
75 | O/G MCC-116 BUS B I/C-2 | 1000A rating | Siemens | ETU45B | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.9-0.95-0.98-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 0.8 | 3.5 |  | 0.9 | 2 |  |  | CB_O/G2_MCC-116_BUS B 1
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 | 12 | 0.4 |  | 12 | 200
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20 | 12
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | 900 | 0.2 |  | 600 | 200
76 | I/C MCC-116 BUS B I/C-2 | 1000A rating | Schneider | MicroLogic 6.0 | L |  | O/L | 0.4-0.45-0.5-0.55-0.6-0.65-0.7-0.8-0.9-1 | 0.5-1-2-4-8-12-16-20-24 | 0.9 | 2 |  | 0.9 | 2 |  |  | CB_O/G2_MCC-116_BUS B 2
[5 empty] | S |  | S/C | 1.5-2-2.5-3-4-5-6-8-10 | 0.1-0.2-0.3-0.4 | Not Available
[5 empty] | I |  | Instantaneous | 2-3-4-6-8-10-12-15 | 50 | Not Available
[5 empty] | G |  | Ground | 0.2-0.3-0.4-0.5-0.6-0.7-0.8-0.9-1.0 | 0.1-0.2-0.3-0.4 | Not Available
77 | O/G PDB-111-A BUS B I/C1 | 1000A rating | Siemens | ETU45B | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.9-0.95-0.98-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 0.8 | 3.5 |  | 0.8 | 3.5 |  |  | CB_I/C1_PDB-111-A_BUS B 1
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 | 12 | 0.4 |  | 12 | 200
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20 | 12
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | 900 | 0.2 |  | 600 | 200
78 | I/C PDB-111-A BUS B I/C1 | 1000A rating | Siemens | ETU45B | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.9-0.95-0.98-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 0.8 | 3.5 |  | 0.8 | 3.5 |  |  | CB_I/C1_PDB-111-A_BUS B 2
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 | 12 | 0.4 |  | 12 | 200
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20 | 12
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | 900 | 0.2 |  | 600 | 200
79 | O/G COOLING WATER PUMP 2 FOR TOWER 1 | 400/1 | ABB | SPAM150C | 51 | I> | P/F | 0.5-0.01-2.5 | 0.05-0.01-1.0 | 20 | 0.04 | DT | 0.9 | 1 | NI |  | O/G_COOLING WATER PUMP 2 FOR TOWER 1
[5 empty] | 50 | I>> | P/F Hs | 0.500-0.010-40.0 | 0.040-0.010-300.0 |  |  |  | 7.32 | 0.05 | DT
[5 empty] | 51N | I0> | E/F | 0.100-0.010-1.00 | 0.050-0.010-30 |  |  |  | 0.2 | 1 | NI
[5 empty] | 50N | I0>> | E/F Hs | 0.100-0.010-10.0 | 0.050-0.010-300.0 | 1 | 0.05 | DT | 0.5 | 0.05 | DT
80 | O/G MCC 112 BUS B I/C1 | 1000A rating | Siemens | ETU45B | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.9-0.95-0.98-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 0.8 | 3.5 |  | 0.8 | 2 |  |  | CB_O/G1_MCC 112 1
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 | 12 | 0.4 |  | 12 | 200
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20 | 12
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | 900 | 0.2 |  | 600 | 200
81 | I/C MCC 112 BUS B I/C1 | 800A rating | Siemens | ETU45B | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.9-0.95-0.98-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 0.8 | 0.1 |  | 0.8 | 2 |  |  | CB_O/G1_MCC 112 2
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 | Not Available
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20 | Not Available
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | Not Available
82 | O/G COOLING WATER PUMP 2 FOR TOWER 2 | 400/1 | ABB | SPAM150C | 51 | I> | P/F | 0.5-0.01-2.5 | 0.05-0.01-1.0 | 20 | 0.04 | DT | 0.9 | 1 | NI |  | CT_O/G_COOLING WATER PUMP 2 FOR TOWER 2
[5 empty] | 50 | I>> | P/F Hs | 0.500-0.010-40.0 | 0.040-0.010-300.0 |  |  |  | 7.32 | 0.05 | DT
[5 empty] | 51N | I0> | E/F | 0.100-0.010-1.00 | 0.050-0.010-30 |  |  |  | 0.2 | 1 | NI
[5 empty] | 50N | I0>> | E/F Hs | 0.100-0.010-10.0 | 0.050-0.010-300.0 | 1 | 0.05 | DT | 0.5 | 0.05 | DT
83 | O/G SCREW COMPRESSOR PNEUMATIC-4 | 400/1 | ABB | SPAM150C | 51 | I> | P/F | 0.5-0.01-2.5 | 0.05-0.01-1.0 | 20 | 0.04 | DT | 0.9 | 1 | NI |  | CT_O/G_SCREW COMPRESSOR PNEUMATIC-4
[5 empty] | 50 | I>> | P/F Hs | 0.500-0.010-40.0 | 0.040-0.010-300.0 |  |  |  | 7.32 | 0.05 | DT
[5 empty] | 51N | I0> | E/F | 0.100-0.010-1.00 | 0.050-0.010-30 |  |  |  | 0.2 | 1 | NI
[5 empty] | 50N | I0>> | E/F Hs | 0.100-0.010-10.0 | 0.050-0.010-300.0 | 1 | 0.05 | DT | 0.5 | 0.05 | DT
84 | O/G IAT SOFT STARTER PANEL | 1000A rating | Siemens | ETU45B | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.9-0.95-0.98-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 0.9 | 21 |  | 0.4 | 2 |  |  | CB_O/G_IAT SOFT STARTER PANEL
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 | 0.6 | 0.4 |  | 2 | 200
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20 | 3
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | 900 | 0.3 |  | 600 | 200
85 | O/G ACID PUMP FOR IAT | 400/1 | ABB | SPAM150C | 51 | I> | P/F | 0.5-0.01-2.5 | 0.05-0.01-1.0 |  |  |  | 0.9 | 1 | NI |  | CT_ACID PUMP FOR IAT
[5 empty] | 50 | I>> | P/F Hs | 0.500-0.010-40.0 | 0.040-0.010-300.0 |  |  |  | 7.32 | 0.05 | DT
[5 empty] | 51N | I0> | E/F | 0.100-0.010-1.00 | 0.050-0.010-30 |  |  |  | 0.2 | 1 | NI
[5 empty] | 50N | I0>> | E/F Hs | 0.100-0.010-10.0 | 0.050-0.010-300.0 |  |  |  | 0.5 | 0.05 | DT
86 | O/G COOLING WATER PUMP 3 FOR TOWER 4 | 400/1 | ABB | SPAM150C | 51 | I> | P/F | 0.5-0.01-2.5 | 0.05-0.01-1.0 | 20 | 0.04 | DT | 0.83 | 1 | NI |  | CT_O/G_COOLING WATER PUMP 3 FOR TOWER 4
[5 empty] | 50 | I>> | P/F Hs | 0.500-0.010-40.0 | 0.040-0.010-300.0 |  |  |  | 6.78 | 0.05 | DT
[5 empty] | 51N | I0> | E/F | 0.100-0.010-1.00 | 0.050-0.010-30 |  |  |  | 0.3 | 1 | NI
[5 empty] | 50N | I0>> | E/F Hs | 0.100-0.010-10.0 | 0.050-0.010-300.0 | 1 | 0.05 | DT | 0.5 | 0.05 | DT
0.415kV PCC - 111
87 | I/C PCC-111_BUS A | 4000A rating | Siemens | ETU45B | L |  | O/L | 0.4-0.45-0.5-0.55-0.6-0.65-0.7-0.8-0.9-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 1 | 21 |  | 0.5 | 2 |  |  | CB_TR-111-A
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 | 10 | 0.4 |  | 2 | 400
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20 | 10 |  |  | - | -
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | 1200 | 0.2 |  | 900 | 400
88 | I/C PCC-111_BUS B | 4000A rating | Siemens | ETU45B | L |  | O/L | 0.4-0.45-0.5-0.55-0.6-0.65-0.7-0.8-0.9-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 1 | 21 |  | 0.5 | 2 |  |  | CB_TR 111-B
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 | 10 | 0.4 |  | 6 | 400
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20 | 10
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | 1200 | 0.2 |  | 1200 | 400
89 | O/G SCREW COMPRESSOR PNEUMATIC-1 | 400/1 | ABB | SPAM150C | 51 | I> | P/F | 0.5-0.01-2.5 | 0.05-0.01-1.0 | 20 | 0.04 | DT | 0.8 | 1 | NI |  | CT_SCREW COMPRESSOR PNEUMATIC-1
[5 empty] | 50 | I>> | P/F Hs | 0.500-0.010-40.0 | 0.040-0.010-300.0 |  |  |  | 6.45 | 0.05 | DT
[5 empty] | 51N | I0> | E/F | 0.100-0.010-1.00 | 0.050-0.010-30 |  |  |  | 0.3 | 1 | NI
[5 empty] | 50N | I0>> | E/F Hs | 0.100-0.010-10.0 | 0.050-0.010-300.0 | 1 | 0.05 | DT | 0.5 | 0.05 | DT
90 | O/G COOLING WATER PUMP 1 FOR TOWER 5 | 400/1 | ABB | SPAM150C | 51 | I> | P/F | 0.5-0.01-2.5 | 0.05-0.01-1.0 | 20 | 0.04 | DT | 0.9 | 1 | NI |  | CT_COOLING WATER PUMP 1 FOR TOWER 5
[5 empty] | 50 | I>> | P/F Hs | 0.500-0.010-40.0 | 0.040-0.010-300.0 |  |  |  | 7.32 | 0.05 | DT
[5 empty] | 51N | I0> | E/F | 0.100-0.010-1.00 | 0.050-0.010-30 |  |  |  | 0.3 | 1 | NI
[5 empty] | 50N | I0>> | E/F Hs | 0.100-0.010-10.0 | 0.050-0.010-300.0 | 1 | 0.05 | DT | 0.5 | 0.05 | DT
91 | O/G MCC-114 BUS A I/C1 | 1000A rating | Siemens | ETU45B | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.9-0.95-0.98-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 0.8 | 3.5 |  | 0.8 | 3.5 |  |  | CB_O/G1_MCC-114 1
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 | 12 | 0.4 |  | 8 | 200
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20 | 12
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | 1200 | 0.2 |  | 600 | 200
92 | I/C MCC-114 BUS A I/C1 | 800A rating | Siemens | ETU45B | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.9-0.95-0.98-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 0.8 | 3.5 |  | 0.8 | 3.5 |  |  | CB_O/G1_MCC-114 2
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 | 12 | 0.4 |  | 6 | 200
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20 | 12
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | 1200 | 0.2 |  | 600 | 200
93 | O/G MCC-112 BUS A I/C2 | 1000A rating | Siemens | ETU45B | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.9-0.95-0.98-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 0.8 | 2 |  | 0.8 | 3.5 |  |  | CB_O/G2_MCC-112 1
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 | 12 | 0.2 |  | 6 | 200
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20 | 8
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | 900 | 0.1 |  | 600 | 200
94 | I/C MCC-112 BUS A I/C2 | 800A rating | Siemens | ETU45B | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.9-0.95-0.98-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 0.9 | 3.5 |  | 0.9 | 3.5 |  |  | CB_O/G2_MCC-112 2
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 | 8 | 0.2 |  | 6 | 200
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20 | 12
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | 900 | 0.1 |  | 600 | 200
95 | O/G MCC-115 BUS A I/C1 | 1000A rating | Siemens | ETU45B | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.9-0.95-0.98-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 0.8 | 3.5 |  | 0.8 | 3.5 |  |  | CB_O/G1_MCC-115 1
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 | 12 | 0.4 |  | 6 | 200
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20 | 12
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | 1200 | 0.2 |  | 600 | 200
96 | I/C MCC-115 BUS A I/C1 | 800A rating | Siemens | ETU45B | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.9-0.95-0.98-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 0.9 | 3.5 |  | 0.9 | 3.5 |  |  | CB_O/G1_MCC-115 2
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 | 8 | 0.2 |  | 8 | 200
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20 | 12
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | 900 | 0.1 |  | 600 | 200
97 | O/G PDB-111 BUS A I/C1 | 1000A rating | Siemens | ETU45B | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.9-0.95-0.98-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 0.8 | 3.5 |  | 0.8 | 3.5 |  |  | CB_I/C1_PDB-111_BUS A 1
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 | 12 | 0.4 |  | 6 | 200
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20 | 12 |  |  | - | -
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | 1200 | 0.2 |  | 600 | 200
99 | I/C PDB-111 BUS A I/C1 | 800A rating | Siemens | ETU45B | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.9-0.95-0.98-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 0.9 | 2 |  | 0.9 | 2 |  |  | CB_I/C1_PDB-111_BUS A 2
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 |  |  |  | 6 | 200
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | 900 | 0.1 |  | 600 | 200
100 | O/G MCC 118 BUS A I/C1 | 1000A rating | Siemens | ETU45B | L |  | O/L | 0.4-0.45-0.5-0.55-0.6-0.65-0.7-0.8-0.9-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 0.8 | 3.5 |  | 0.8 | 2 |  |  | CB_O/G1_MCC 118 (STG) 1
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 | 12 | 0.4 |  | 8 | 200
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20 | 12
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | 1200 | 0.2 |  | 900 | 200
101 | I/C MCC 118 BUS A I/C1 | 630A rating | Siemens | MCCB | L |  | O/L | 0.8-0.1-1.0 | 1 | 0.8 | 3.5 |  | 1 | 1 |  |  | CB_O/G1_MCC 118 (STG) 2
[5 empty] | I |  | Instantaneous | 5-1-10 | 0.01 | 1200 | 0.2 |  | 10 | 0.01
102 | O/G MCC-111 BUS A I/C1 | 1000A rating | Siemens | ETU45B | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.9-0.95-0.98-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 1 | 2 |  | 1 | 2 |  |  | CB_O/G1_MCC-111 1
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 | 12 | 0.4 |  | 2 | 200
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20 | 8 |  |  | - | -
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | 900 | 0.1 |  | 900 | 200
103 | I/C MCC-111 BUS A I/C1 | 800A rating | Siemens | ETU45B | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.9-0.95-0.98-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 1 | 2 |  | 1 | 2 |  |  | CB_O/G1_MCC-111 2
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 | 12 | 0.4 |  | 2 | 200
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20 | 8 |  |  | - | -
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | 900 | 0.1 |  | 900 | 200
104 | O/G MCC-113 BUS A I/C1 | 1000A rating | Siemens | ETU45B | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.9-0.95-0.98-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 0.8 | 2 |  | 0.8 | 2 |  |  | CB_O/G1_MCC-113 1
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 | 12 | 0.2 |  | 6 | 200
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20 | 8 |  |  | - | -
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | 900 | 0.1 |  | 900 | 200
105 | I/C MCC-113 BUS A I/C1 | 800A rating | Siemens | ETU45B | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.9-0.95-0.98-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 0.8 | 2 |  | 0.8 | 2 |  |  | CB_O/G1_MCC-113 2
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 | 12 | 0.2 |  | 6 | 200
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20 | 8 |  |  | - | -
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | 900 | 0.1 |  | 0.9 | 200
106 | O/G PDB-112 BUS A I/C2 | 1000A rating | Siemens | ETU45B | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.9-0.95-0.98-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 0.8 | 3.5 |  | 0.8 | 2 |  |  | CB_I/C2_PDB-112_BUS A 1
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 | 12 | 0.4 |  | 4 | 200
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20 | 12 |  |  | - | -
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | 1200 | 0.2 |  | 900 | 200
107 | I/C PDB-112 BUS A I/C2 | 800A rating | Siemens | ETU45B | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.9-0.95-0.98-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 0.8 | 2 |  | 0.8 | 2 |  |  | CB_I/C2_PDB-112_BUS A 2
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 | 12 | 0.2 |  | 4 | 200
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20 | 8 |  |  | - | -
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | 900 | 0.1 |  | 900 | 200
108 | O/G SCREW COMPRESSOR PNEUMATIC-2 | 400/1 | ABB | SPAM150C | 51 | I> | P/F | 0.5-0.01-2.5 | 0.05-0.01-1.0 | 20 | 0.04 | DT | 0.9 | 1 | NI |  | CT_O/G_SCREW COMPRESSOR PNEUMATIC-2
[5 empty] | 50 | I>> | P/F Hs | 0.500-0.010-40.0 | 0.040-0.010-300.0 |  |  |  | 7.32 | 0.05 | DT
[5 empty] | 51N | I0> | E/F | 0.100-0.010-1.00 | 0.050-0.010-30 |  |  |  | 0.3 | 1 | NI
[5 empty] | 50N | I0>> | E/F Hs | 0.100-0.010-10.0 | 0.050-0.010-300.0 | 1 | 0.05 | DT | 0.5 | 0.05 | DT
109 | O/G CLDC MCC | 1000A rating | Siemens | ETU45B | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.9-0.95-0.98-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 0.8 | 2 |  | 0.8 | 2 |  |  | CB_O/G_CLDC MCC 1
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 | 12 | 0.2 |  | 4 | 200
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20 | 8 |  |  | - | -
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | 900 | 0.1 |  | 900 | 200
110 | I/C CLDC MCC | 400A rating | Siemens | MCCB | L |  | O/L | 0.8-0.1-1.0 | 1 | 1 | 1 |  | 1 | 1 |  | 400 A MCCB | CB_O/G_CLDC MCC 2
[5 empty] | I |  | Instantaneous | 5-1-10 | 0.01 | 5 | 0.01 |  | 5 | 0.01
111 | O/G HRM CLDC MCC | 160A rating | Siemens | MCCB | L |  | O/L | 0.8-0.1-1.0 | 1 | 1 | 1 |  | 1 | 1 |  |  | CB_O/G_HRM_CLDC MCC
[5 empty] | I |  | Instantaneous | 5-1-10 | 0.01 | 5 | 0.01 |  | 5 | 0.01
99 | O/G FAT SOFT STARTER PANEL | 630A rating | NO LSIG | [13 empty] | CB_O/G_FAT SOFT STARTER PANEL
112 | O/G FAT PUMP | 400A rating | Siemens | MCCB | L |  | O/L | 0.8-0.1-1.0 | 1 | 1 | 1 |  | 1 | 1 |  |  | CB_FAT PUMP
[5 empty] | I |  | Instantaneous | 5-1-10 | 0.01 | 5 | 0.01 |  | 5 | 0.01
101 | O/G DT SOFT STARTER PANEL | 630A rating | NO LSIG | [13 empty] | CB_O/G_DT SOFT STARTER PANEL
113 | O/G DT PUMP | 400A rating | Siemens | MCCB | L |  | O/L | 0.8-0.1-1.0 | 1 | 1 | 1 |  | 1 | 1 |  |  | CB_O/G_DT PUMP
[5 empty] | I |  | Instantaneous | 5-1-10 | 0.01 | 5 | 0.01 |  | 5 | 0.01
0.415kV PDB - 111
114 | O/G HRM PDB-111 BUS A | 160A rating | Siemens | MCCB | L |  | O/L | 1 | 1 | 1 | 1 |  | 1 | 1 |  |  | CB_HRM_PDB-111_BUS A
[5 empty] | I |  | Instantaneous | 1 | 0.01 | 1 | 0.01 |  | 1 | 0.01
115 | O/G BATTERY CHARGER I/C1 | 63A rating | Siemens | MCCB | L |  | O/L | 1 | 1 | 1 | 1 |  | 1 | 1 |  |  | CB_O/G1_BATTERY CHARGER
[5 empty] | I |  | Instantaneous | 1 | 0.01 | 1 | 0.01 |  | 1 | 0.01
116 | O/G UPS 40 KVA I/C1 | 160A rating | Siemens | MCCB | L |  | O/L | 1 | 1 | 1 | 1 |  | 1 | 1 |  |  | CB_O/G1_UPS 40 KVA
[5 empty] | I |  | Instantaneous | 1 | 0.01 | 1 | 0.01 |  | 1 | 0.01
117 | O/G UPS 30 KVA I/C1 | 160A rating | Siemens | MCCB | L |  | O/L | 1 | 1 | 1 | 1 |  | 1 | 1 |  |  | CB_O/G1_UPS 30 KVA
[5 empty] | I |  | Instantaneous | 1 | 0.01 | 1 | 0.01 |  | 1 | 0.01
107 | O/G ROOF TOP SOLAR |  | Not Available |  | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.9-0.95-0.98-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | [7 empty] | CB_SOLAR
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500
118 | O/G UPS 40 KVA I/C2 | 160A rating | Siemens | MCCB | L |  | O/L | 1 | 1 | 1 | 1 |  | 1 | 1 |  |  | CB_O/G1_UPS 40 KVA
[5 empty] | I |  | Instantaneous | 1 | 0.01 | 1 | 0.01 |  | 1 | 0.01
119 | O/G UPS 30 KVA I/C2 | 160A rating | Siemens | MCCB | L |  | O/L | 1 | 1 | 1 | 1 |  | 1 | 1 |  |  | CB_O/G1_UPS 30 KVA
[5 empty] | I |  | Instantaneous | 1 | 0.01 | 1 | 0.01 |  | 1 | 0.01
0.415kV PDB - 112
120 | O/G PNV BLOWER | 160A rating | Siemens | MCCB | L |  | O/L | 1 | 1 | 1 | 1 |  | 1 | 1 |  |  | CB_O/G_PNV BLOWER
[5 empty] | I |  | Instantaneous | 1 | 0.01 | 1 | 0.01 |  | 1 | 0.01
121 | O/G HRM PDB-112 BUS B | 160A rating | Siemens | MCCB | L |  | O/L | 1 | 1 | 1 | 1 |  | 1 | 1 |  |  | CB_HRM_PDB-112_BUS B
[5 empty] | I |  | Instantaneous | 1 | 0.01 | 1 | 0.01 |  | 1 | 0.01
0.415kV MCC - 111
121 | O/G HGP TR-1 | 400A rating | Siemens | MCCB | L |  | O/L | 0.8-0.1-1.0 | 1 | 1 | 1 |  | 1 | 1 |  |  | CB_O/G_HGP TR-1 1
[5 empty] | I |  | Instantaneous | 5-1-10 | 0.01 | 5 | 0.01 |  | 5 | 0.01
122 | I/C HGP TR-1 | 200A rating | Siemens | MCCB | L |  | O/L | 0.8-0.1-1.0 | 1 | 1 | 1 |  | 1 | 1 |  |  | CB_O/G_HGP TR-1 2
[5 empty] | I |  | Instantaneous | 5-1-10 | 0.01 | 5 | 0.01 |  | 5 | 0.01
114 | O/G HRM MCC-111 BUS A |  | Not Available |  | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.9-0.95-0.98-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | [7 empty] | CB_HRM_MCC-111_BUS A
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500
115 | O/G HRM MCC-111 BUS B |  | Not Available |  | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.9-0.95-0.98-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | [7 empty] | CB_HRM_MCC-111_BUS B
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500
123 | O/G HGP TR-2 | 400A rating | Siemens | MCCB | L |  | O/L | 0.8-0.1-1.0 | 1 | 1 | 1 |  | 1 | 1 |  |  | CB_O/G_HGP-2 TR 1
[5 empty] | I |  | Instantaneous | 5-1-10 | 0.01 | 5 | 0.01 |  | 5 | 0.01
124 | I/C HGP TR-2 | 200A rating | Siemens | MCCB | L |  | O/L | 0.8,0.9,1.0 | 1 | 1 | 1 |  | 1 | 1 |  |  | CB_O/G_HGP-2 TR 2
[5 empty] | I |  | Instantaneous | 5-1-10 | 0.01 | 5 | 0.01 |  | 5 | 0.01
125 | O/G HGP TR-3 | 400A rating | Siemens | MCCB | L |  | O/L | 0.8-0.1-1.0 | 1 | 1 | 1 |  | 1 | 1 |  |  | CB_O/G_HGP-3 TR 1
[5 empty] | I |  | Instantaneous | 5-1-10 | 0.01 | 5 | 0.01 |  | 5 | 0.01
126 | I/C HGP TR-3 | 200A rating | Siemens | MCCB | L |  | O/L | 0.8,0.9,1.0 | 1 | 1 | 1 |  | 1 | 1 |  |  | CB_O/G_HGP-3 TR 2
[5 empty] | I |  | Instantaneous | 5-1-10 | 0.01 | 5 | 0.01 |  | 5 | 0.01
0.415kV MCC - 112
120 | O/G HRM MCC-112 BUS A |  | Not Available |  | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.9-0.95-0.98-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | [7 empty] | CB_HRM_MCC-112_BUS A
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500
121 | O/G HRM MCC-112 BUS B |  | Not Available |  | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.9-0.95-0.98-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | [7 empty] | CB_HRM_MCC-112_BUS B
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500
0.415kV MCC - 113
122 | O/G HRM MCC-113 BUS A |  | Not Available |  | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.9-0.95-0.98-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | [7 empty] | CB_HRM_MCC-113_BUS A
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500
123 | O/G HRM MCC-113 BUS B |  | Not Available |  | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.9-0.95-0.98-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | [7 empty] | CB_HRM_MCC-113_BUS B
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500
0.415kV MCC - 114
124 | O/G HRM MCC-114 BUS A |  | Not Available |  | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.9-0.95-0.98-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | [7 empty] | CB_HRM_MCC-114_BUS A
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500
125 | O/G HRM MCC-114 BUS B |  | Not Available |  | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.9-0.95-0.98-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | [7 empty] | CB_HRM_MCC-114_BUS B
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500
0.415kV MCC - 115
126 | O/G HRM MCC-115 BUS A |  | Not Available |  | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.9-0.95-0.98-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | [7 empty] | CB_HRM_MCC-115_BUS A
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500
127 | O/G HRM MCC-115 BUS B |  | Not Available |  | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.9-0.95-0.98-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | [7 empty] | CB_HRM_MCC-115_BUS B
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500
0.415kV MCC - 116
128 | O/G HRM MCC-116 BUS A |  | Not Available |  | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.9-0.95-0.98-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | [7 empty] | CB_HRM_MCC-116_BUS A
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500
129 | O/G HRM MCC-116 BUS B |  | Not Available |  | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.9-0.95-0.98-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | [7 empty] | CB_HRM_MCC-116_BUS B
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500
0.415kV MCC - 118
130 | O/G HRM MCC-118 BUS A |  | Not Available |  | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.9-0.95-0.98-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | [7 empty] | CB_HRM_MCC-118_BUS A
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500
131 | O/G HRM MCC-118 BUS B |  | Not Available |  | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.9-0.95-0.98-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | [7 empty] | CB_HRM_MCC-118_BUS B
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500

## SS-1 (hidden)
SS - 1
Department |  |  | Author |  | Status | [7 empty] | Date |  | Lang.
Power Consulting |  |  | Pritul Panchal |  | Rev A | [7 empty] | 2023-12-28 |  | en
sr. No | FeederType or Location | CT Ratio Amps | Relay Make | Relay Type | Relay NEMA Code | IEC Code | Prot Type | Relay Range |  | Exisitng Setting |  |  | Proposed Setting |  |  | Remark
[8 empty] | Plug setting range | Time setting range (s) / TMs range | Plug setting | Time setting (s) / TMs | Charact eristic | Plug setting | Time setting (s) / TMs | Charact eristic
0.415kV PYROTEC PCC
1 | I/C AUX TR 2 (PYROTEC PCC) | 2000A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  |  |  |  | 1 |  |  |  | CB_O/G_AUX TR 2
[5 empty] | S |  | S/C | 11kA & 14kA | 0.025
2 | O/G1 ZE PYROTEC MCC | 2000A rating | MG | MicroLogic 6.0 | L |  | O/L | 0.4-0.45-0.5-0.55-0.6-0.65-0.7-0.8-0.9-1 | 0.5-1-2-4-8-12-16-20-24 | 0.8 | 12 |  | 0.5 | 8 |  |  | CB_O/G1_ZE PYROTEC MCC 1
[5 empty] | S |  | S/C | 1.5-2-2.5-3-4-5-6-8-10 | 0.1-0.2-0.3-0.4 | 5 | 0.4 |  | 5 | 0.2
[5 empty] | I |  | Instantaneous | 2-3-4-6-8-10-12-15 | 50
[5 empty] | G |  | Ground | 0.2-0.3-0.4-0.5-0.6-0.7-0.8-0.9-1.0 | 0.1-0.2-0.3-0.4 | 0.4 | 0.6 |  | 0.8 | 0.2
3 | O/G1 301A MCC | 2000A rating | MG | MicroLogic 6.0 | L |  | O/L | 0.4-0.45-0.5-0.55-0.6-0.65-0.7-0.8-0.9-1 | 0.5-1-2-4-8-12-16-20-24 | 0.5 | 12 |  | 0.6 | 12 |  |  | CB_O/G1_ 301A MCC 1
[5 empty] | S |  | S/C | 1.5-2-2.5-3-4-5-6-8-10 | 0.1-0.2-0.3-0.4 | 5 | 0.3 |  | 5 | 0.2
[5 empty] | I |  | Instantaneous | 2-3-4-6-8-10-12-15 | 50 | 0.3
[5 empty] | G |  | Ground | 0.2-0.3-0.4-0.5-0.6-0.7-0.8-0.9-1.0 | 0.1-0.2-0.3-0.4 | 0.2 | 0.2 |  | 800 | 0.2
4 | O/G MG PANEL (SS-1) | 2000A rating | MG | MicroLogic 6.0 | L |  | O/L | 0.4-0.45-0.5-0.55-0.6-0.65-0.7-0.8-0.9-1 | 0.5-1-2-4-8-12-16-20-24 | 0.5 | 12 |  | 0.8 | 4 |  |  | CB_O/G_MG PANEL (SS-1) 1
[5 empty] | S |  | S/C | 1.5-2-2.5-3-4-5-6-8-10 | 0.1-0.2-0.3-0.4 | 5 | 0.3 |  | 5 | 0.4
[5 empty] | I |  | Instantaneous | 2-3-4-6-8-10-12-15 | 50 | 0.3
[5 empty] | G |  | Ground | 0.2-0.3-0.4-0.5-0.6-0.7-0.8-0.9-1.0 | 0.1-0.2-0.3-0.4 | 0.2 | 0.2 |  | 800 | 0.4
5 | O/G1 COOLING TOWER MCC | 2000A rating | MG | MicroLogic 6.0 | L |  | O/L | 0.4-0.45-0.5-0.55-0.6-0.65-0.7-0.8-0.9-1 | 0.5-1-2-4-8-12-16-20-24 | 0.9 | 12 |  | 0.9 | 12 |  |  | CB1_O/G1_COOLING TOWER MCC
[5 empty] | S |  | S/C | 1.5-2-2.5-3-4-5-6-8-10 | 0.1-0.2-0.3-0.4 | 4 | 0.4 |  | 4 | 0.4
[5 empty] | I |  | Instantaneous | 2-3-4-6-8-10-12-15 | 50
[5 empty] | G |  | Ground | 0.2-0.3-0.4-0.5-0.6-0.7-0.8-0.9-1.0 | 0.1-0.2-0.3-0.4 | 0.3 | 0.4 |  | 600 | 0.4
0.415kV MG PANEL MCC
6 | I/C MG PANEL MCC BUS A | 1250A rating | L&T | SR18G Release | L |  | O/L | 0.50-0.60-0.65-0.70-0.75-0.80-0.85-0.90-0.95-1.00 | 2.5 | 1 | 2.5 |  | 1 | 2.5 |  |  | CB1_O/G_TO SS 1
[5 empty] | S |  | S/C | 2-3-4-5-6-7-8-9-10 | 20-60-100-160-200-260-300-400-500-600 (ms) | 7 | 0.6 |  | 5 | 0.4
[5 empty] | I |  | Instantaneous | 6-12 | 0.025 | 12
[5 empty] | G |  | Ground | 0.2-0.3-0.4-0.5-0.6 | 100-200-300-400 (ms) | 0.4 | 0.2 |  | 0.6 | 0.4
7 | O/G Cadmium Old MG MCC | 800A rating | MG | MicroLogic 6.0 | L |  | O/L | 0.50-0.60-0.65-0.70-0.75-0.80-0.85-0.90-0.95-1.00 | 2.5 | 2 | 10 |  | 0.5 | 2 |  |  | CB1_O/G_Cadmium Old MG MCC
[5 empty] | S |  | S/C | 2-3-4-5-6-7-8-9-10 | 20-60-100-160-200-260-300-400-500-600 (ms) |  |  |  | 5 | 200
[5 empty] | I |  | Instantaneous | 6-12 | 0.025
[5 empty] | G |  | Ground | 0.2-0.3-0.4-0.5-0.6 | 100-200-300-400 (ms) |  |  |  | 0.2 | 200
8 | O/G2 PYROTEC LP MCC | 800A rating | MG | MicroLogic 6.0 | L |  | O/L | 0.50-0.60-0.65-0.70-0.75-0.80-0.85-0.90-0.95-1.00 | 2.5 | 1.5 | 10 |  | 1 | 2 |  |  | CB1_O/G2_PYROTEC LP MCC
[5 empty] | S |  | S/C | 2-3-4-5-6-7-8-9-10 | 20-60-100-160-200-260-300-400-500-600 (ms) |  |  |  | 5 | 200
[5 empty] | I |  | Instantaneous | 6-12 | 0.025
[5 empty] | G |  | Ground | 0.2-0.3-0.4-0.5-0.6 | 100-200-300-400 (ms) |  |  |  | 0.8 | 0.2
9 | O/G2 COOLING TOWER MCC | 800A rating | MG | MicroLogic 6.0 | L |  | O/L | 0.50-0.60-0.65-0.70-0.75-0.80-0.85-0.90-0.95-1.00 | 2.5 | 1.5 | 10 |  | 1 | 2 |  |  | CB1_O/G2_COOLING TOWER MCC
[5 empty] | S |  | S/C | 2-3-4-5-6-7-8-9-10 | 20-60-100-160-200-260-300-400-500-600 (ms) |  |  |  | 5 | 200
[5 empty] | I |  | Instantaneous | 6-12 | 0.025
[5 empty] | G |  | Ground | 0.2-0.3-0.4-0.5-0.6 | 100-200-300-400 (ms) |  |  |  | 0.8 | 200
10 | O/G2 LEACHING 201B2 MCC | 800A rating | MG | MicroLogic 6.0 | L |  | O/L | 0.50-0.60-0.65-0.70-0.75-0.80-0.85-0.90-0.95-1.00 | 2.5 | 2 | 10 |  | 1 | 2 |  |  | CB1_O/G2_LEACHING 201B2 MCC
[5 empty] | S |  | S/C | 2-3-4-5-6-7-8-9-10 | 20-60-100-160-200-260-300-400-500-600 (ms) |  |  |  | 8 | 200
[5 empty] | I |  | Instantaneous | 6-12 | 0.025
[5 empty] | G |  | Ground | 0.2-0.3-0.4-0.5-0.6 | 100-200-300-400 (ms) |  |  |  | 0.8 | 200
11 | I/C MG PANEL (SS-1) | 1250A rating | L&T | SR18G Release | L |  | O/L | 0.50-0.60-0.65-0.70-0.75-0.80-0.85-0.90-0.95-1.00 | 2.5 | 1 | 2.5 |  | 0.8 | 2.5 |  |  | CB_O/G_MG PANEL (SS-1) 2
[5 empty] | S |  | S/C | 2-3-4-5-6-7-8-9-10 | 20-60-100-160-200-260-300-400-500-600 (ms) | 7 | 0.6 |  | 7 | 0.4
[5 empty] | I |  | Instantaneous | 6-12 | 0.025 | 12
[5 empty] | G |  | Ground | 0.2-0.3-0.4-0.5-0.6 | 100-200-300-400 (ms) | 0.4 | 0.2 |  | 0.6 | 0.4
12 | O/G 301B MCC | 800A rating | MG | MicroLogic 6.0 | L |  | O/L | 0.50-0.60-0.65-0.70-0.75-0.80-0.85-0.90-0.95-1.00 | 2.5 | 2 | 10 |  | 1 | 2 |  |  | CB_I/C_301B MCC 1
[5 empty] | S |  | S/C | 2-3-4-5-6-7-8-9-10 | 20-60-100-160-200-260-300-400-500-600 (ms) |  |  |  | 5 | 200
[5 empty] | I |  | Instantaneous | 6-12 | 0.025
[5 empty] | G |  | Ground | 0.2-0.3-0.4-0.5-0.6 | 100-200-300-400 (ms) |  |  |  | 0.8 | 200
13 | O/G LR MILL | 250A rating | Schneider | TCVS250N MCCB | L |  | O/L | 0.8-0.1-1.0 |  | 1 |  |  | 1 | 1 |  |  | CB_I/C_LR MILL 1
[5 empty] | I |  | Instantaneous | 5-1-10 | 0.025 | 1250 |  |  | 5 | 0.025
14 | O/G WARTSILA + CISF | 800A rating | MG | MicroLogic 6.0 | L |  | O/L | 0.50-0.60-0.65-0.70-0.75-0.80-0.85-0.90-0.95-1.00 | 2.5 | 1 | 10 |  | 1 | 2 |  |  | CB_L_WARTSILA + CISF 1
[5 empty] | S |  | S/C | 2-3-4-5-6-7-8-9-10 | 20-60-100-160-200-260-300-400-500-600 (ms) |  |  |  | 5 | 0.2
[5 empty] | I |  | Instantaneous | 6-12 | 0.025
[5 empty] | G |  | Ground | 0.2-0.3-0.4-0.5-0.6 | 100-200-300-400 (ms) |  |  |  | 0.8 | 0.2
15 | I/C WARTSILA + CISF |  | Not Available | [13 empty] | CB_L_WARTSILA + CISF 2
15 | O/G1 DM PLANT | 800A rating | MG | MicroLogic 6.0 | L |  | O/L | 0.50-0.60-0.65-0.70-0.75-0.80-0.85-0.90-0.95-1.00 | 2.5 | 0.5 | 10 |  | 1 | 2 |  |  | CB_O/G1_DM PLANT 1
[5 empty] | S |  | S/C | 2-3-4-5-6-7-8-9-10 | 20-60-100-160-200-260-300-400-500-600 (ms) |  |  |  | 4 | 0.2
[5 empty] | I |  | Instantaneous | 6-12 | 0.025
[5 empty] | G |  | Ground | 0.2-0.3-0.4-0.5-0.6 | 100-200-300-400 (ms) |  |  |  | 0.2 | 200
16 | O/G1 NEW CADMIUM MCC | 800A rating | MG | MicroLogic 6.0 | L |  | O/L | 0.50-0.60-0.65-0.70-0.75-0.80-0.85-0.90-0.95-1.00 | 2.5 | 2 | 10 |  | 1 | 8 |  |  | CB_O/G1_NEW CADMIUM MCC 1
[5 empty] | S |  | S/C | 2-3-4-5-6-7-8-9-10 | 20-60-100-160-200-260-300-400-500-600 (ms) |  |  |  | 5 | 0.2
[5 empty] | I |  | Instantaneous | 6-12 | 0.025
[5 empty] | G |  | Ground | 0.2-0.3-0.4-0.5-0.6 | 100-200-300-400 (ms) |  |  |  | 0.8 | 0.2
17 | O/G SUPPLY TO NEW DPH | 800A rating | MG | MicroLogic 6.0 | L |  | O/L | 0.50-0.60-0.65-0.70-0.75-0.80-0.85-0.90-0.95-1.00 | 2.5 | 1 | 10 |  | 1 | 8 |  |  | CB_I/C_SUPPLY TO NEW DPH 1
[5 empty] | S |  | S/C | 2-3-4-5-6-7-8-9-10 | 20-60-100-160-200-260-300-400-500-600 (ms) |  |  |  | 5 | 0.2
[5 empty] | I |  | Instantaneous | 6-12 | 0.025
[5 empty] | G |  | Ground | 0.2-0.3-0.4-0.5-0.6 | 100-200-300-400 (ms) |  |  |  | 0.8 | 0.2
18 | O/G L&T MCC (MCC-3) | 800A rating | MG | MicroLogic 6.0 | L |  | O/L | 0.50-0.60-0.65-0.70-0.75-0.80-0.85-0.90-0.95-1.00 | 2.5 | 2 | 10 |  | 1 | 8 |  |  | CB_L&T MCC (MCC-3) 1
[5 empty] | S |  | S/C | 2-3-4-5-6-7-8-9-10 | 20-60-100-160-200-260-300-400-500-600 (ms) |  |  |  | 5 | 0.2
[5 empty] | I |  | Instantaneous | 6-12 | 0.025
[5 empty] | G |  | Ground | 0.2-0.3-0.4-0.5-0.6 | 100-200-300-400 (ms) |  |  |  | 0.2 | 0.2
0.415kV 301A MCC
19 | I/C1 301A MCC (From SS-1) | 1250A rating | L&T | UW-MTX1.5G | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.85-0.9-0.95-1 | 0.5-1-2-4-6-12-18-24-30 | 1 | 12 |  | 0.8 | 6 |  |  | CB_O/G1_ 301A MCC 2
[5 empty] | S |  | S/C | 0.6-1-1.5-2-3-4-6-8-10-12 | 20-100-200-300-400 (ms) | 4 | 0.4 |  | 4 | 0.2
[5 empty] | I |  | Instantaneous | 1.5-2-3-4-6-8-10-12-15 | 0.025 | OFF
[5 empty] | G |  | Ground | 0.2-0.3-0.4-0.5-0.6 | 0.1-0.2-0.3-0.4-1 (s) | 0.6 | 0.1 |  | 0.6 | 0.2
20 | I/C2 301A MCC (From SS-4) | 1250A rating | L&T | UW-MTX1.5G | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.85-0.9-0.95-1 | 0.5-1-2-4-6-12-18-24-30 | 0.85 | 12 |  | 0.8 | 6 |  |  | CB_OG2_ ZE 301A MCC (SS-4) 1
[5 empty] | S |  | S/C | 0.6-1-1.5-2-3-4-6-8-10-12 | 20-100-200-300-400 (ms) | 3 | 0.4 |  | 4 | 0.2
[5 empty] | I |  | Instantaneous | 1.5-2-3-4-6-8-10-12-15 | 0.025 | OFF
[5 empty] | G |  | Ground | 0.2-0.3-0.4-0.5-0.6 | 0.1-0.2-0.3-0.4-1 (s) | 0.5 | 0.2 |  | 0.6 | 0.2
21 | O/G HRM ZE PIROTEC MCC | 250A rating | L&T | SFU | [12 empty] | CT_HRM_301A MCC
0.415kV Cadmium Old MG MCC
22 | I/C Cadmium Old MG MCC | 600A rating | MG | MicroLogic 6.0 | L |  | O/L | 0.4-0.45-0.5-0.55-0.6-0.65-0.7-0.8-0.9-1 | 0.5-1-2-4-8-12-16-20-24 | 600 |  |  | 0.5 | 2 |  |  | CB2_O/G_Cadmium Old MG MCC
[5 empty] | S |  | S/C | 1.5-2-2.5-3-4-5-6-8-10 | 0.1-0.2-0.3-0.4 |  |  |  | 5 | 0.2
[5 empty] | I |  | Instantaneous | 2-3-4-6-8-10-12-15 | 50
[5 empty] | G |  | Ground | 0.2-0.3-0.4-0.5-0.6-0.7-0.8-0.9-1.0 | 0.1-0.2-0.3-0.4 |  |  |  | 0.2 | 0.2
23 | O/G HRM Cadmium Old MG MCC | 25A rating | MG | B664 | L |  | O/L | 1 | 1 |  |  |  | 1 | 1 |  |  | CB_O/G_HRM_Cadmium Old MG MCC
[5 empty] | I |  | Instantaneous | 1 | 0.01 | 23 |  |  | 1 | 0.01
0.415kV 301B MCC
25 | O/G HRM 301B MCC | 250A rating | L&T | SFU | [12 empty] | CT_HRM_301B MCC
0.415kV LR MILL MCC
24 | I/C LR MILL | 630A rating | Siemens | MCCB | L |  | O/L | 0.8-0.1-1.0 | 1 |  |  |  | 1 | 1 |  |  | CB_I/C_LR MILL 2
[5 empty] | I |  | Instantaneous | 5-1-10 | 0.01 |  |  |  | 5 | 0.01
26 | O/G HRM LR MILL | [15 empty] | CT_HRM_LR MILL
0.415kV DM PLANT MCC
25 | I/C1 DM PLANT (From SS-1) | 800A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 0.75 |  |  | 0.75 |  |  |  | CB_O/G1_DM PLANT 2
[5 empty] | S |  | S/C | 4.7kA & 6kA | 0.025 |  |  |  | 4.7 | 0.025
26 | I/C2 DM PLANT (From SS-7) | Supply Removed | [14 empty] | CB_O/G2_DM NEW MCC-1 2
29 | O/G HRM DM PLANT |  | Not Available | [13 empty] | CT_HRM_DM PLANT
0.415kV NEW CADMIUM MCC
27 | I/C1 NEW CADMIUM MCC (From SS-1) | 1000A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 0.75 |  |  | 0.75 |  |  |  | CB_O/G1_NEW CADMIUM MCC 2
[5 empty] | S |  | S/C | 5.7kA & 7.2kA | 0.025 |  |  |  | 5.7 | 0.025
28 | I/C2 STANDBY CADMIUM 2EPZ 701 (From SS-4) | 1000A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 0.75 |  |  | 0.75 |  |  |  | CB_O/G2_STANDBY CADMIUM 2EPZ 701 2
[5 empty] | S |  | S/C | 5.7kA & 7.2kA | 0.025 |  |  |  | 5.7 | 0.025
|  | 800/5 | Alstom | CDG14 | 51N | I0> | EF | 10% .. 320% | 0.1 .. 1.0 |  |  |  | 0.2 | 1 | EI |  | CT_O/G2_STANDBY CADMIUM 2EPZ 701
32 | O/G HRM NEW CADMIUM MCC | 21A Rating | Siemens | SIRIUS | [5 empty] | 21 |  |  | 21 |  |  |  | CT_O/G_HRM_NEW CADMIUM MCC
0.415kV SUPPLY TO NEW DPH MCC
33 | I/C SUPPLY TO NEW DPH |  | Not Available | [13 empty] | CB_I/C_SUPPLY TO NEW DPH 2
34 | O/G HRM SUPPLY TO NEW DPH CRANE |  | Not Available | [13 empty] | CB_HRM_SUPPLY TO NEW DPH CRANE
0.415kV L&T MCC (MCC-3)
29 | I/C L&T MCC (MCC-3) | 1600A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 0.75 |  |  | 0.75 |  |  |  | CB_L&T MCC (MCC-3) 2
[5 empty] | S |  | S/C | 8.8kA & 11.5kA | 0.025 |  |  |  | 8.8 | 0.025
37 | O/G HRM L&T MCC (MCC-3) |  | Not Available | [13 empty] | CT_HRM_L&T MCC (MCC-3)
30 | O/G HBF MCC | 1000A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 0.75 |  |  | 0.75 |  |  |  | CB_HBF MCC
[5 empty] | S |  | S/C | 5.7kA & 7.2kA | 0.025 |  |  |  | 5.7 | 0.025
0.415kV ZE PIROTEC MCC
31 | I/C1 ZE PYROTEC MCC (From SS-1) | 1600A rating | MG | MicroLogic 6.0 | L |  | O/L | 0.4-0.45-0.5-0.55-0.6-0.65-0.7-0.8-0.9-1 | 0.5-1-2-4-8-12-16-20-24 | 0.6 | 8 |  | 0.5 | 8 |  |  | CB_O/G1_ZE PYROTEC MCC 2
[5 empty] | S |  | S/C | 1.5-2-2.5-3-4-5-6-8-10 | 0.1-0.2-0.3-0.4 | 3 | 0.4 |  | 5 | 0.2
[5 empty] | I |  | Instantaneous | 2-3-4-6-8-10-12-15 | 50 | 0.2 | 0.2
[5 empty] | G |  | Ground | 0.2-0.3-0.4-0.5-0.6-0.7-0.8-0.9-1.0 | 0.1-0.2-0.3-0.4 |  |  |  | 0.8 | 0.2
32 | I/C2 ZE PYROTEC MCC (From SS-2) | 1600A rating | MG | MicroLogic 6.0 | L |  | O/L | 0.4-0.45-0.5-0.55-0.6-0.65-0.7-0.8-0.9-1 | 0.5-1-2-4-8-12-16-20-24 | 0.6 | 8 |  | 0.5 | 4 |  |  | CB2_O/G2_ZE PIROTEC MCC (SS-2)
[5 empty] | S |  | S/C | 1.5-2-2.5-3-4-5-6-8-10 | 0.1-0.2-0.3-0.4 | 3 | 0.4 |  | 5 | 0.2
[5 empty] | I |  | Instantaneous | 2-3-4-6-8-10-12-15 | 50
[5 empty] | G |  | Ground | 0.2-0.3-0.4-0.5-0.6-0.7-0.8-0.9-1.0 | 0.1-0.2-0.3-0.4 | 0.2 | 0.2 |  | 0.5 | 0.2
41 | O/G HRM ZE PIROTEC MCC | 250A rating | L&T | SFU | [12 empty] | CT_HRM_ZE PIROTEC MCC BUS A
0.415kV COOLING TOWER BUS
33 | I/C2 COOLING TOWER MCC (From MG Panel SS-1) | 400A rating | Siemens | ETU12 | L |  | O/L | 0.4-0.45-0.5-0.63-0.7-0.8-0.9-0.95-1 | 2.5-4-6-8-10-14-17-20-25-30 | 1 |  |  | 1 | 2.5 |  |  | CB2_O/G2_COOLING TOWER MCC
[5 empty] | I |  | Instantaneous | 1.25-1.5-2-3-4-5-6-8-10-11 | 0.02 | 4 |  |  | 5 | 1
[5 empty] | G |  | Ground | 0.6-0.7-0.8-0.9-1.0 | 0.1-0.2-0.3-0.4 | 1 | 0.3 |  | 0.6 | 0.1
34 | I/C1 COOLING TOWER MCC (From Pyrotec PCC SS-1) | 400A rating | Siemens | ETU12 | L |  | O/L | 0.4-0.45-0.5-0.63-0.7-0.8-0.9-0.95-1 | 2.5-4-6-8-10-14-17-20-25-30 | 0.95 |  |  | 1 | 2.5 |  |  | CB2_O/G1_COOLING TOWER MCC
[5 empty] | I |  | Instantaneous | 1.25-1.5-2-3-4-5-6-8-10-11 | 0.02 | 5 |  |  | 5 | 1
[5 empty] | G |  | Ground | 0.6-0.7-0.8-0.9-1.0 | 0.1-0.2-0.3-0.4 | 0.6 | 0.3 |  | 0.6 | 0.1
44 | O/G HRM COOLING TOWER BUS A | 50A Rating | Siemens | SIRIUS | [5 empty] | 50 | [6 empty] | CT_HRM_COOLING TOWER BUS A
0.415kV NEW HBF MCC
45 | I/C NEW HBF MCC | 160A Rating | Siemens | SFU | [5 empty] | 160 |  |  | 160 |  |  |  | CB_O/G_NEW HBF MCC
46 | O/G HRM NEW HBF MCC | [15 empty] | CT_O/G_HRM_NEW HBF MCC
0.415kV OLD HBF MCC | [16 empty] | CT_O/G_1_STG 1
45 | I/C OLD HBF MCC | 100A Rating | Siemens | SFU | [5 empty] | 100 |  |  | 100 |  |  |  | CB_O/G_OLD HBF MCC
46 | O/G HRM NEW HBF MCC | [15 empty] | CT_O/G_HRM_OLD HBF MCC

## SS-2 (hidden)
SS - 2
Department |  |  | Author |  | Status | [7 empty] | Date |  | Lang.
Power Consulting |  |  | Pritul Panchal |  | Rev A | [7 empty] | 2023-12-28 |  | en
sr. No | FeederType or Location | CT Ratio Amps | Relay Make | Relay Type | Relay NEMA Code | IEC Code | Prot Type | Relay Range |  | Exisitng Setting |  |  | Proposed Setting |  |  | Remark
[8 empty] | Plug setting range | Time setting range (s) / TMs range | Plug setting | Time setting (s) / TMs | Charact eristic | Plug setting | Time setting (s) / TMs | Charact eristic
0.415kV SS-2
1 | I/C AUX TR-3 Bus-A | 3200A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 0.8 |  |  | 0.8 | - |  |  | CB_O/G_AUX TR-3
[5 empty] | S |  | S/C | 17.5kA & 22kA | 0.025 | - | - |  | - | -
|  | 2500/5 | Alstom | CDG14 | 51N | I0> | EF | 10% .. 320% | 0.1 .. 1.0 | 1 | 0.85 | EI | 0.8 | 1 | EI |  | CT_O/G_AUX TR-3
2 | I/C AUX TR-4 Bus-B | 3200A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 0.75 |  |  | 0.75 | - |  |  | CB_O/G_AUX TR-4
[5 empty] | S |  | S/C | 17.5kA & 22kA | 0.025 | - | - |  | - | -
|  | 2500/5 | Alstom | CDG14 | 51N | I0> | EF | 10% .. 320% | 0.1 .. 1.0 | 1 | 1 | EI | 0.2 | 1 | EI |  | CT_O/G_AUX TR-4
3 | O/G1 ROASTER II L&T 2EPZ 501 (From SS-2) | 1250A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 1 |  |  | 1 | - |  |  | CB1_O/G1_ROASTER II L&T 2EPZ 501
[5 empty] | S |  | S/C | 7kA & 8.9kA | 0.025 | - | - |  | 8.9 | 0.025
|  | 800/5 | Alstom | CDG14 | 51N | I0> | EF | 10% .. 320% | 0.1 .. 1.0 | 0.5 | 0.2 | EI | 0.1 | 1 | EI |  | CT_O/G1_ROASTER II L&T 2EPZ 501
4 | O/G ACID PLANT II | 1250A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 1 |  |  | 1 | - |  |  | CB1_O/G_ACID PLANT II
[5 empty] | S |  | S/C | 7kA & 8.9kA | 0.025 | - | - |  | 8.9 | 0.025
|  | 800/5 | Alstom | CDG14 | 51N | I0> | EF | 10% .. 320% | 0.1 .. 1.0 | 0.5 | 0.5 | EI | 0.8 | 1 | EI |  | CT_O/G_ACID PLANT II
5 | O/G ROASTER II ID FAN | 1250A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 0.9 |  |  | 0.8 | - |  |  | CB1_O/G_ROASTER II ID FAN
[5 empty] | S |  | S/C | 7kA & 8.9kA | 0.025 | - | - |  | - | -
|  | 300/5 | Alstom | CDG12 | 51N |  | Standby EF | 15% & 20% | 0.1 .. 1.0 | 1 | 0.7 | LI | 0.2 | 0.1 | LI |  | CT_O/G_ACID PLANT II
|  | 300/5 | Alstom | CAU29 | 50N | I0>> | E/F Hs | 5-20% 10-40% 20-80% 50-200% 100-400% | 0.06-0.6 0.2-1.0 0.5-3.0 2.0-10.0 5.0-25.0 or 10-60 | 130% | 25 | DT | 4 | 0.02 | DT
6 | I/C ROASTER II ID FAN | 1250A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 1 |  |  | 1 | - |  |  | CB2_O/G_ROASTER II ID FAN
[5 empty] | S |  | S/C | 7kA & 8.9kA | 0.025 | - | - |  | - | -
7 | O/G1 CADMIUM BUILDING PCC II | 1000A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 0.95 |  |  | 0.95 | - |  |  | CB1_O/G1_CADMIUM BUILDING PCC II
[5 empty] | S |  | S/C | 5.7kA & 7.2kA | 0.025 | - | - |  | 5.7 | 0.025
|  | 600/5 | Alstom | CDG14 | 51N | I0> | EF | 10% .. 320% | 0.1 .. 1.0 | 0.5 | 0.35 | EI | 0.1 | 1 | EI |  | CT_O/G1_CADMIUM BUILDING PCC II
8 | O/G1 ROASTER II GE MCC | 1250A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 0.9 |  |  | 0.75 | - |  |  | CB1_O/G1_ROASTER II GE MCC
[5 empty] | S |  | S/C | 7kA & 8.9kA | 0.025 | - | - |  | 7 | 0.025
|  | 600/5 | Alstom | CDG14 | 51N | I0> | EF | 10% .. 320% | 0.1 .. 1.0 | 0.5 | 0.5 | EI | 0.1 | 1 | EI |  | CT_O/G1_ROASTER II GE MCC
9 | O/G IR-1 COMP | 800A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 0.9 |  |  | 0.75 | - |  |  | CB_O/G_IR-1 COMP
[5 empty] | S |  | S/C | 4.7kA & 6kA | 0.025 | - | - |  | 6 | 0.025
|  | 600/5 | Alstom | CDG14 | 51N | I0> | EF | 10% .. 320% | 0.1 .. 1.0 | 0.5 | 0.65 | EI | 0.1 | 0.65 | EI |  | CT_O/G_IR-1 COMP
10 | O/G2 TGT SPARE SUPPLY (From SS-2) | 1000A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 0.75 |  |  | 1 | - |  |  | CB1_O/G2_TGT SPARE SUPPLY
[5 empty] | S |  | S/C | 5.7kA & 7.2kA | 0.025 | - | - |  | 7.2 | 0.025
|  | 600/5 | Alstom | CDG14 | 51N | I0> | EF | 10% .. 320% | 0.1 .. 1.0 | 0.5 | 0.5 | EI | 0.1 | 1 | EI |  | CT_O/G2_TGT SPARE SUPPLY
11 | O/G2 ZE PIROTEC MCC (From SS-2) | 1250A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 0.75 |  |  | 1.25 | - |  |  | CB1_O/G2_ZE PIROTEC MCC (SS-2)
[5 empty] | S |  | S/C | 7kA & 8.9kA | 0.025 | - | - |  | - | -
|  | 800/5 | Alstom | CDG14 | 51N | I0> | EF | 10% .. 320% | 0.1 .. 1.0 | 0.5 | 0.85 | EI | 0.1 | 0.25 | EI |  | CT_O/G2_ZE PIROTEC MCC (SS-2)
12 | O/G PHE PCC TIE (From SS-2) | 1250A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 1 |  |  | 1 | - |  |  | CB1_O/G_PHE PCC_TIE
[5 empty] | S |  | S/C | 7kA & 8.9kA | 0.025 | - | - |  | - | -
|  | 1000/5 | Alstom | CDG14 | 51N | I0> | EF | 10% .. 320% | 0.1 .. 1.0 | 0.5 | 1 | EI | 0.1 | 1 | EI |  | CT_O/G_PHE PCC_TIE
13 | O/G SS-7 (From SS-2) | 1250A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 1 |  |  | 1 | - |  |  | CB1_O/G_SS-7 MV SG 7 SY-22712
[5 empty] | S |  | S/C | 7kA & 8.9kA | 0.025 | - | - |  | - | -
|  | 1250/5 | Alstom | CDG14 | 51N | I0> | EF | 10% .. 320% | 0.1 .. 1.0 | 1 | 0.25 | EI | 0.2 | 0.25 | EI |  | CT_O/G_SS-7 MV SG 7 SY-22712
14 | O/G COMPRESSOR HOUSE MCC SIEMENS (From SS-2) | 1250A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 1 |  |  | 1 | - |  |  | CB_I/C_COMPRESSOR HOUSE MCC SIEMENS
[5 empty] | S |  | S/C | 7kA & 8.9kA | 0.025 | - | - |  | 8.9 | 0.025
|  | 800/5 | Alstom | CDG14 | 51N | I0> | EF | 10% .. 320% | 0.1 .. 1.0 | 1 | 0.1 | EI | 0.2 | 0.5 | EI |  | CT_I/C_COMPRESSOR HOUSE MCC SIEMENS
15 | O/G1 PYROTEC LP MCC (From SS-2) | 1250A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 0.9 |  |  | 1 | - |  |  | CB1_O/G1_PYROTEC LP MCC
[5 empty] | S |  | S/C | 7kA & 8.9kA | 0.025 | - | - |  | - | -
|  | 800/5 | Alstom | CDG14 | 51N | I0> | EF | 10% .. 320% | 0.1 .. 1.0 | 1 | 0.1 | EI | 0.2 | 0.5 | EI |  | CT_I/C_NEW PURIFICATION MCC-P
0.415kV ROASTER II L&T 2EPZ 501
16 | I/C1 ROASTER II L&T 2EPZ 501 (From SS-2) | 1000A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 1 |  |  | 1 | - |  |  | CB2_O/G1_ROASTER II L&T 2EPZ 501
[5 empty] | S |  | S/C | 5.7kA & 7.2kA | 0.025 | - | - |  | 7.2 | 0.025
17 | I/C2 R2 LT MCC (SS-4) | 1000A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 1 |  |  | 1 | - |  |  | CB1_O/G2_R2 LT MCC
[5 empty] | S |  | S/C | 5.7kA & 7.2kA | 0.025 | - | - |  | 7.2 | 0.025
18 | O/G HRM ROASTER II L&T 2EPZ 501 | 1000A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 1 |  |  | 1 | - |  |  | CB_O/G_HRM_ROASTER II L&T 2EPZ 501
[5 empty] | S |  | S/C | 5.7kA & 7.2kA | 0.025 | - | - |  | 7.2 | 0.025
|  | 150/5 | BOCR | 3ez | 50 | I>> | P/F Hs | 15A-180A | 1 .. 30 | 110A | 10 | DT | 110A | 500ms |  |  | CT_O/G_HRM_ROASTER II L&T 2EPZ 501
0.415kV ACID PLANT II
19 | I/C ACID PLANT II | 1000A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 0.75 |  |  | 0.75 | - |  |  | CB2_O/G_ACID PLANT II
[5 empty] | S |  | S/C | 5.7kA & 7.2kA | 0.025 | - | - |  | 7.2 | 0.025
20 | O/G HRM ACID PLANT II | 160A rating | Siemens | MCCB | L |  | O/L | 1 | 1 |  |  |  | 1 | 1 |  |  | CB_O/G_HRM_ACID PLANT II
[5 empty] | I |  | Instantaneous | 1 | 0.01 | 1 | 0.025 |  | 1 | 0.01
0.415kV CADMIUM BUILDING PCC II
| I/C1 CADMIUM BUILDING PCC II (From SS-2) | 400A rating | L&T | SFU | [12 empty] | F_O/G1_CADMIUM BUILDING PCC II
| I/C2 CADMIUM BUILDING PCC II (From SS-4) | 400A rating | L&T | SFU | [12 empty] | F_O/G1_CADMIUM BUILDING PCC II
0.415kV ROASTER II GE MCC
21 | I/C1 ROASTER II GE MCC (From SS-2) | 1000A rating | GE | MPACT M-PRO 17 Plus | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.9-1 | Fixed | 1 | 0.1 |  | 1 |  |  |  | CB2_O/G1_ROASTER II GE MCC
[5 empty] | S |  | S/C | 1.5-2-3-4-6-8-10-12 | 0.1-0.2-0.4-0.5-0.6-0.8-1.0 (s)
[5 empty] | I |  | Instantaneous | OFF-2-3-4-6-8-10-12 | 0.025
[5 empty] | G |  | Ground | OFF-0.4-0.6-0.8-1 | 0.1-0.2-0.4-0.6-0.8-1.0 (s)
22 | I/C2 ROASTER II GE MCC (From PHE PCC) | 1000A rating | GE | MPACT M-PRO 17 Plus | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.9-1 | Fixed | 1 | 0.1 |  | 1 |  |  |  | CB2_O/G2_ROASTER II GE MCC
[5 empty] | S |  | S/C | 1.5-2-3-4-6-8-10-12 | 0.1-0.2-0.4-0.5-0.6-0.8-1.0 (s)
[5 empty] | I |  | Instantaneous | OFF-2-3-4-6-8-10-12 | 0.025
[5 empty] | G |  | Ground | OFF-0.4-0.6-0.8-1 | 0.1-0.2-0.4-0.6-0.8-1.0 (s)
23 | O/G HRM ROASTER II GE MCC (From SS-2) | 630A rating | Siemens | MCCB | L |  | O/L | 1 |  |  |  |  | 1 |  |  |  | CB_O/G_HRM_ROASTER II GE MCC
[5 empty] | I |  | Instantaneous | 1 | 0.025 | 1 | 0.025 |  | 5 | 0.01
0.415kV TGT PLANT MCC
24 | I/C2 TGT SPARE SUPPLY (From SS-2) | 100A rating | Siemens | MCCB | L |  | O/L | 0.8-0.1-1.0 | 1 |  |  |  | 0.8 | 1 |  |  | CB2_O/G2_TGT SPARE SUPPLY
[5 empty] | I |  | Instantaneous | 5-1-10 | 0.01 | 1 | 0.01 |  | 5 | 0.01
0.415kV PHE PCC
25 | I/C PHE PCC TIE (From SS-2) | 1000A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 1 |  |  | 1 | - |  |  | CB2_O/G_PHE PCC_TIE
[5 empty] | S |  | S/C | 5.7kA & 7.2kA | 0.025 | - | - |  | - | -
|  | 1000/5 | EASUN ROYROLLE | TJM20 | 51N | I0> | EF | 20% .. 80% | 0.1 .. 1.0 | 10 | 0.2 | VI | 0.5 | 0.2 | VI |  | CT_O/G_PHE PCC_TIE 2
26 | I/C AUX TR 12 | 3200A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 1 |  |  | 0.75 | - |  |  | CB_O/G_AUX TR 12
[5 empty] | S |  | S/C | 5.7kA & 7.2kA | 0.025 | - | - |  | - | -
|  | 3000/5 | EASUN ROYROLLE | TJM20 | 51N | I0> | EF | 10% .. 40% | 0.1 .. 1.0 | 10 | 0.8 | VI | 0.2 | 1 | VI |  | CT_O/G_AUX TR 12
27 | O/G2 ROASTER II GE MCC (From PHE PCC) | 800A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 0.9 |  |  | 0.9 | - |  |  | CB1_O/G2_ROASTER II GE MCC
[5 empty] | S |  | S/C | 4.7kA & 6kA | 0.025 |  |  |  | 4.7 | 0.025
28 | O/G BCH PCC (From PHE PCC) | 1250A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 0.9 |  |  | 0.9 | - |  |  | CB1_O/G_BCH PCC
[5 empty] | S |  | S/C | 7kA & 8.9kA | 0.025 |  |  |  | 7 | 0.025
29 | O/G1 PH2 MCC (From PHE PCC) | 1250A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 0.75 |  |  | 0.75 | - |  |  | CB1_O/G1_PH2 MCC
[5 empty] | S |  | S/C | 7kA & 8.9kA | 0.025 |  |  |  | 5.7 | 0.025
|  | 400/5 | EASUN ROYROLLE | TJM20 | 51N | I0> | EF | 10% .. 40% | 0.1 .. 1.0 | 10 | 0.5 | VI | 0.2 | 1 | VI |  | CT_I/C_PH2 MCC
30 | O/G COMP L&T MCC (From PHE PCC) | 1250A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 0.75 |  |  | 0.75 | - |  |  | CB1_I/C_COMP L&T MCC
[5 empty] | S |  | S/C | 7kA & 8.9kA | 0.025 |  |  |  | 5.7 | 0.025
|  | 400/5 | EASUN ROYROLLE | TJM20 | 51N | I0> | EF | 10% .. 40% | 0.1 .. 1.0 | 10 | 0.2 | VI | 0.2 | 1 | VI |  | CT_I/C_COMP L&T MCC
31 | O/G NEW COMPRESSOR PANEL (From PHE PCC) | 2000A rating | MG Enerpact | MicroLogic 6.0 | L |  | O/L | 0.4-0.45-0.5-0.55-0.6-0.65-0.7-0.8-0.9-1 | 0.5-1-2-4-8-12-16-20-24 | 0.6 | 8 |  | 0.6 | 8 |  |  | CB1_O/G_NEW COMPRESSOR PANEL
[5 empty] | S |  | S/C | 1.5-2-2.5-3-4-5-6-8-10 | 0.1-0.2-0.3-0.4 | 2 | Inst |  | 2 | 0.2
[5 empty] | I |  | Instantaneous | 2-3-4-6-8-10-12-15 | 50
[5 empty] | G |  | Ground | 0.2-0.3-0.4-0.5-0.6-0.7-0.8-0.9-1.0 | 0.1-0.2-0.3-0.4 | 0.1 | Inst |  | 500 | 0.2
32 | O/G1 DM PLANT MCC-3 (From PHE PCC) | 1000A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 0.75 |  |  | 0.9 | - |  |  | CB1_O/G1_DM PLANT MCC-3
[5 empty] | S |  | S/C | 5.7kA & 7.2kA | 0.025 |  |  |  | 5.7 | 0.025
|  | 400/5 | EASUN ROYROLLE | TJM20 | 51N | I0> | EF | 10% .. 40% | 0.1 .. 1.0 | 0.9 | 0.2 | VI | 0.2 | 1 | VI |  | CT_O/G1_DM PLANT MCC-3
33 | O/G1 PH NO 3 MCC (From PHE PCC) | 1250A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 0.9 |  |  | 0.9 | - |  |  | CB1_O/G1_PH NO 3 MCC
[5 empty] | S |  | S/C | 7kA & 8.9kA | 0.025 |  |  |  | 7 | 0.025
|  | 1250/5 | Universal Electrics Ltd | R-1638 IOC | 51N | I0> | EF | 10% .. 100% | 0.1 .. 1.0 | 0.9 |  | EI | 0.2 | 0.4 | EI |  | CT1_I/C_PH NO 3 MCC
0.415kV BCH PCC
34 | I/C BCH PCC | 1250A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 0.9 |  |  | 0.9 | - |  |  | CB2_O/G_BCH PCC
[5 empty] | S |  | S/C | 7kA & 8.9kA | 0.025 |  |  |  | 7 | 0.025
| O/G BPTG PCC |  | Not Available | [13 empty] | CB1_O/G_BPTG
| I/C BPTG PCC |  | Not Available | [13 empty] | CB1_O/G_BPTG
35 | O/G HRM BCH PCC | 200A rating | Siemens | MCCB | L |  | O/L | 1 |  |  |  |  | 1 | 1 |  |  | CB_O/G_HRM_BCH PCC
[5 empty] | I |  | Instantaneous | 1 | 0.025 | 1 | 0.025 |  | 1 | 0.025
0.415kV PH2 MCC
36 | I/C1 PH2 MCC (From PHE PCC) | 1250A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 0.75 |  |  | 0.75 | - |  |  | CB2_O/G1_PH2 MCC
[5 empty] | S |  | S/C | 7kA & 8.9kA | 0.025 | - | - |  | 5.7 | 0.025
|  | 250/5 | Alstom | CDG14 | 51N | I0> | EF | 10% .. 320% | 0.1 .. 1.0 | 0.5 | 0.4 | EI | 0.2 | 0.4 | EI |  | CT2_I/C_PH2 MCC
37 | I/C2 PH2 MCC (From SS-4) | 1000A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 1 |  |  | 0.75 | - |  |  | CB2_O/G2_PH2 MCC
[5 empty] | S |  | S/C | 5.7kA & 7.2kA | 0.025 | - | - |  | 5.7 | 0.025
38 | O/G HRM PH2 MCC | 110A rating | Siemens | MCCB | L |  | O/L | 1 | [8 empty] | CB_O/G_HRM_PH2 MCC
[5 empty] | I |  | Instantaneous | 1 | 0.025 | 1 | 0.025
|  | 150/5 | BOCR | 3ez | 50 | I>> | P/F Hs | 15A-180A | 1 .. 30 | 10A | 10 | DT |  |  |  |  | CT_O/G_HRM_PH2 MCC
0.415kV COMP L&T MCC
39 | I/C COMP L&T MCC (From PHE PCC) | 1000A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 0.75 |  |  | 0.75 |  |  |  | CB2_I/C_COMP L&T MCC
[5 empty] | S |  | S/C | 5.7kA & 7.2kA | 0.025 | - | - |  | 5.7 | 0.025
0.415kV NEW COMPRESSOR PANEL
40 | O/G NEW COMPRESSOR PANEL (From PHE PCC) | 800A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 0.75 |  |  | 1 |  |  |  | CB2_O/G_NEW COMPRESSOR PANEL
[5 empty] | S |  | S/C | 4.7kA & 6kA | 0.025 |  |  |  | 4.7 | 0.025
|  | 400/5 | EASUN ROYROLLE | TJM20 | 51N | I0> | EF | 10% .. 40% | 0.1 .. 1.0 | 20 | 0.9 | VI | 0.5 | 1 | VI |  | CT_O/G_NEW COMPRESSOR PANEL
0.415kV COMPRESSOR HOUSE MCC SIEMENS
| I/C COMPRESSOR HOUSE MCC SIEMENS (From SS-2) | 400A rating | L&T | SFU | [12 empty] | CB_O/G_COMPRESSOR HOUSE MCC SIEMENS
|  | 400/5 | EASUN ROYROLLE | TJM20 | [12 empty] | CT_O/G_COMPRESSOR HOUSE MCC SIEMENS
0.415kV NEW PURIFICATION MCC-P
41 | I/C1 PYROTEC LP MCC (From SS-2) | 1600A rating | MG | MicoLogic 6.0A | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.9-0.95-0.98-1 | 0.5-1-2-4-8-12-16-20-24 | 0.8 | 12 |  | 0.5 | 2 |  |  | CB2_O/G1_PYROTEC LP MCC
[5 empty] | S |  | S/C | 1.5-2-2.5-3-4-5-6-8-10 | 0.1-0.2-0.3-0.4 (s) | 3 | 0.4 |  | 5 | 0.2
[5 empty] | I |  | Instantaneous | 2-3-4-6-8-10-12-15-OFF | 0.02 | - | -
[5 empty] | G |  | Ground | 0.2-0.3-0.4-0.5-0.6-0.7-0.8-0.9-1.0 | 0.1-0.2-0.3-0.4 (s) | 0.6 | 0.4 |  | 0.6 | 0.2
42 | I/C2 PYROTEC LP MCC (From SS-1) | 1600A rating | MG | MicoLogic 6.0A | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.9-0.95-0.98-1 | 0.5-1-2-4-8-12-16-20-24 | 0.7 | 12 |  | 0.5 | 2 |  |  | CB2_O/G2_PYROTEC LP MCC
[5 empty] | S |  | S/C | 1.5-2-2.5-3-4-5-6-8-10 | 0.1-0.2-0.3-0.4 (s) | - | - |  | 5 | 0.2
[5 empty] | I |  | Instantaneous | 2-3-4-6-8-10-12-15-OFF | 0.02 | - | -
[5 empty] | G |  | Ground | 500-640-720-800-880-960-1040-1120-1200 | 0.1-0.2-0.3-0.4 (s) | 0.64 | 0.4 |  | 0.64 | 0.2

## SS-3 (hidden)
SS - 3
Department |  |  | Author |  | Status | [7 empty] | Date |  | Lang.
Power Consulting |  |  | Pritul Panchal |  | Rev A | [7 empty] | 2023-12-28 |  | en
sr. No | FeederType or Location | CT Ratio Amps | Relay Make | Relay Type | Relay NEMA Code | IEC Code | Prot Type | Relay Range |  | Exisitng Setting |  |  | Proposed Setting |  |  | Remark
[8 empty] | Plug setting range | Time setting range (s) / TMs range | Plug setting | Time setting (s) / TMs | Charact eristic | Plug setting | Time setting (s) / TMs | Charact eristic
0.415kV SS-3
1 | I/C AUX TR 5 | 3200A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 0.9 |  |  | 1 | - |  |  | CB_O/G_AUX TR 5
[5 empty] | S |  | S/C | 17.5kA & 22kA | 0.025 | - | - |  | - | -
|  | 3200/5 | Alstom | CDG14 | 51N | I0> | EF | 10% .. 320% | 0.1 .. 1.0 | 0.5 | 1 | EI | 0.2 | 0.1 | EI |  | CT_AUX TR 5
2 | O/G JAROSITE FILTER PRESS MCC (From SS-3) | 1600A rating | L&T | UW-MTX1G | L |  | O/L | OFF- 0.4-0.5-0.6-0.7-0.8-0.85-0.9-0.95-1 | 0.5-1-2-4-6-12-18-24-30 | 1 | 12 |  | 0.5 | 12 |  |  | CB1_O/G_JAROSITE FILTER PRESS MCC
[5 empty] | S |  | S/C | 0.6-1-1.5-2-3-4-6-8-10-12 | 20-100-200-300-400 (ms) | 4 | 0.4 |  | 2 | 0.2
[5 empty] | I |  | Instantaneous | OFF-1.5-2-3-4-6-8-10-12-15 | 0.025 | - | -
[5 empty] | G |  | Ground | OFF-0.2-0.3-0.4-0.5-0.6 | 0.1-0.2-0.3-0.4-1 | 0.6 | 0.1 |  | 0.5 | 0.2
3 | O/G CAKE TREATMENT PLANT (From SS-3) | 1000A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 0.75 |  |  | 0.75 | - |  |  | CB1_O/G_CAKE TREATMENT PLANT
[5 empty] | S |  | S/C | 5.7kA & 7.2kA | 0.025 | - | - |  | - | -
|  | 1000/5 | Alstom | CDG14 | 51N | I0> | EF | 10% .. 320% | 0.1 .. 1.0 | 0.5 | 0.2 | EI | 0.2 | 0.5 | EI |  | CT_O/G_CAKE TREATMENT PLANT
4 | O/G MCTP MCC-2 (From SS-3) | 1000A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 1 |  |  | 1 | - |  |  | CB1_O/G_MCTP MCC-2
[5 empty] | S |  | S/C | 5.7kA & 7.2kA | 0.025 | - | - |  | 7 | 0.025
|  | 1000/5 | Alstom | CDG14 | 51N | I0> | EF | 10% .. 120% | 0.1 .. 1.0 | 0.5 | 0.5 | EI | 0.3 | 0.25 | EI |  | CT_O/G_MCTP MCC-2
5 | O/G PDB (From SS-3) | 800A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 0.9 |  |  | 0.9 | - |  |  | CB1_O/G_PDB
[5 empty] | S |  | S/C | 4.7kA & 6kA | 0.025 | - | - |  | - | -
|  | 600/5 | Alstom | CDG14 | 51N | I0> | EF | 10% .. 120% | 0.1 .. 1.0 | 0.5 | 0.2 | EI | 0.1 | 0.2 | EI |  | CT_O/G_PDB
6 | I/C PDB | 250A rating | Siemens | MCCB | L |  | O/L | 0.8-0.1-1.0 |  |  |  |  | 1 | - |  |  | CB2_O/G_PDB
[5 empty] | I |  | Instantaneous | 5-1-10 | 0.025 | 1 | 0.025 |  | - | -
7 | O/G ZINC DUST (From SS-3) | 800A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 0.75 |  |  | 1 | - |  |  | CB1_O/G_ZINC DUST
[5 empty] | S |  | S/C | 4.7kA & 6kA | 0.025 | - | - |  | 6 | 0.025
|  | 400/5 | Alstom | CDG14 | 51N | I0> | EF | 10% .. 120% | 0.1 .. 1.0 | 0.5 | 0.2 | EI | 0.2 | 0.5 | EI |  | CT_O/G_ZINC DUST
8 | I/C ZINC DUST | 250A rating | Siemens | MCCB | L |  | O/L | 0.8-0.1-1.0 |  |  |  |  | 1 | - |  |  | CB2_O/G_ZINC DUST
[5 empty] | I |  | Instantaneous | 5-1-10 | 0.025 | 1 | 0.025 |  | 5 | 0.01
9 | O/G ACID LOADING MCC (From SS-3) | 1000A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 0.75 |  |  | 0.75 | - |  |  | CB_O/G_ACID LOADING MCC
[5 empty] | S |  | S/C | 5.7kA & 7.2kA | 0.025 | - | - |  | 8.9 | 0.025
|  | 1000/5 | Alstom | CDG14 | 51N | I0> | EF | 10% .. 120% | 0.1 .. 1.0 | 0.5 | 0.2 | EI | 0.2 | 0.5 | EI |  | CT_O/G_ACID LOADING MCC
10 | O/G STAND BY ETP (From SS-3) | 800A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 0.75 |  |  | 0.75 | - |  |  | CB1_O/G_STAND BY ETP
[5 empty] | S |  | S/C | 4.7kA & 6kA | 0.025 | - | - |  | - | -
|  | 800/5 | Alstom | CDG14 | 51N | I0> | EF | 10% .. 120% | 0.1 .. 1.0 | 0.5 | 0.2 | EI | 0.2 | 0.5 | EI |  | CT_O/G_STAND BY ETP
0.415kV JAROSITE FILTER PRESS MCC
11 | I/C JAROSITE FILTER PRESS MCC | 1600/1 | Areva | MICOM P127 | 51 | I> | P/F | 0.10 .. 25.0 | 0.025 .. 1.5 | 0.8 | 0.025 | NI | 1 | 1.5 | VI |  | CT_O/G_JAROSITE FILTER PRESS MCC
[5 empty] | 50 | I>> | P/F Hs | 0.5 .. 40.00 | 0.010 .. 1.5 | 4 | 0.025 | DMT | 1.5 | 0.2 | DMT
[5 empty] | 51N | I0> | EF | 0.01 .. 8.00 | 0.025 .. 1.5 | 0.2 | 0.025 | NI
[5 empty] | 50N | I0>> | E/F Hs | 0.01 .. 8.00 | 0.010 .. 1.5 | 0.4 | 0.1 | DMT | 0.5 | 0.2 | DMT
12 | O/G HRM JAROSITE FILTER PRESS MCC |  | SIEMENS | SIMOCODE PRO-V 3UF7010 | 51 | I> | P/F | [9 empty] | CB_O/G_HRM_JAROSITE FILTER PRESS MCC
[5 empty] | 50 | I>> | P/F Hs
[5 empty] | 51N | I0> | EF
[5 empty] | 50N | I0>> | E/F Hs
0.415kV MCTP MCC-1
12 | I/C CAKE TREATMENT PLANT | 1250A rating | SIEMENS | ETU15D Release | L |  | O/L | 0.5-0.55-0.6-0.65-0.7-0.75-0.8-0.85-0.9-1 | 10 (s) | 1 |  |  | 0.5 | 10 |  |  | CB2_O/G_CAKE TREATMENT PLANT
[5 empty] | S |  | S/C | 2-3-4-5-6-7-8 | 0.025 | 6 |  |  | 5 | 0.025
14 | O/G HRM MCTP MCC-1 | 250A rating | L&T | SFU | [12 empty] | F_O/G_HRM_MCTP MCC-1
15 | O/G MCTP MCC-3 | 200A rating | L&T | SFU | [12 empty] | F1_O/G_MCTP MCC-3
0.415kV MCTP MCC-3
16 | I/C MCTP MCC-3 | 250A rating | L&T | SFU | [12 empty] | F2_O/G_MCTP MCC-3
17 | O/G HRM MCTP MCC-3 | 63A rating | L&T | SFU | [12 empty] | F_HRM_MCTP MCC-3
0.415kV MCTP MCC-2
13 | I/C MCTP MCC-2 | 1000A rating | SIEMENS | ETU15D Release | L |  | O/L | 0.4-0.45-0.5-0.55-0.6-0.65-0.7-0.8-0.9-1 | 2-3.5-5.5-8-10-14-17-21-25-30 (s) | 0.8 | 3.5 |  | 0.45 | 2 |  |  | CB2_O/G_MCTP MCC-2
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | 0.02-100-200-300-400 (ms) | 12 | 0.4 |  | 4 | 200
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 0.025 | 12
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 (ms) | 1200 | 0.2 |  | 600 | 200
19 | O/G HRM MCTP MCC-2 | 800A rating | L&T | SFU | [12 empty] | F_HRM_MCTP MCC-2
0.415kV ACID LOADING MCC-1
14 | I/C ACID LOADING MCC-1 | 200A rating | Siemens | MCCB | L |  | O/L | 0.8-0.1-1.0 |  |  |  |  | 1 |  |  |  | CB_O/G_ACID LOADING MCC-1
[5 empty] | I |  | Instantaneous | 5-1-10 | 0.025 | 1 | 0.025 |  | 5 | 0.025
15 | O/G HRM ACID LOADING MCC-1 |  | Siemens | MPCB SIEMENS OLR - 20 A SET | L |  | O/L | 1 | [8 empty] | R_HRM_ACID LOADING MCC-1
[5 empty] | I |  | Instantaneous | 1 | 0.025 | 1 | 0.025
0.415kV ACID LOADING MCC-1
16 | I/C ACID LOADING MCC-2 | 200A rating | Siemens | MCCB | L |  | O/L | 0.8-0.1-1.0 |  |  |  |  | 1 |  |  |  | CB_O/G_ACID LOADING MCC-2
[5 empty] | I |  | Instantaneous | 5-1-10 | 0.025 | 1 | 0.025 |  | 5 | 0.025

## ETP PCC (hidden)
ETP PCC
Department |  |  | Author |  | Status | [7 empty] | Date |  | Lang.
Power Consulting |  |  | Pritul Panchal |  | Rev A | [7 empty] | 2023-12-28 |  | en
sr. No | FeederType or Location | CT Ratio Amps | Relay Make | Relay Type | Relay NEMA Code | IEC Code | Prot Type | Relay Range |  | Exisitng Setting |  |  | Proposed Setting |  |  | Remark
[8 empty] | Plug setting range | Time setting range (s) / TMs range | Plug setting | Time setting (s) / TMs | Charact eristic | Plug setting | Time setting (s) / TMs | Charact eristic
0.415kV ETP PCC
1 | I/C AUX TR 10 | 2000A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 0.8 |  |  | 1 | - |  |  | CB_O/G_AUX TR 10
[5 empty] | S |  | S/C | 11kA & 14kA | 0.025 | - | - |  | - | -
|  | 2000/5 | Alstom | CDG14 | 51N | I0> | EF | 10% .. 320% | 0.1 .. 1.0 | 0.75 | 0.85 | EI | 0.2 | 1 | EI |  | CT_O/G_AUX TR 10
2 | O/G STAND BY ETP (From ETP PCC) | 800A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 0.9 |  |  | 0.9 | - |  |  | CB_O/G_STAND BY ETP
[5 empty] | S |  | S/C | 4.7kA & 6kA | 0.025 | - | - |  | - | -
|  | 800/5 | Alstom | CDG14 | 51N | I0> | EF | 10% .. 120% | 0.1 .. 1.0 | 0.5 | 0.3 | EI | 0.2 | 0.5 | EI |  | CT_O/G_AUX TR 10
3 | O/G PIROTEC PCC | 800A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 0.9 |  |  | 0.9 | - |  |  | CB_PIROTEC PCC
[5 empty] | S |  | S/C | 4.7kA & 6kA | 0.025 | - | - |  | - | -
|  | 600/5 | Alstom | CDG14 | 51N | I0> | EF | 10% .. 120% | 0.1 .. 1.0 | 0.5 | 1 | EI | 0.2 | 0.5 | EI |  | CT1_PIROTEC PCC
4 | O/G EMAC MCC | 800A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 0.75 |  |  | 1 | - |  |  | CB_O/G_EMAC MCC
[5 empty] | S |  | S/C | 4.7kA & 6kA | 0.025 | - | - |  | 7 | 0.025
|  | 600/5 | Alstom | CDG14 | 51N | I0> | EF | 10% .. 120% | 0.1 .. 1.0 | 0.5 | 0.3 | EI | 0.2 | 0.5 | EI |  | CT_I/C_EMAC MCC
5 | O/G SIEMENS MCC | 800A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 0.9 |  |  | 1 | - |  |  | CB_O/G_SIEMENS MCC
[5 empty] | S |  | S/C | 4.7kA & 6kA | 0.025 | - | - |  | - | -
|  | 800/5 | Alstom | CDG14 | 51N | I0> | EF | 10% .. 120% | 0.1 .. 1.0 | 0.5 | 1 | EI | 0.2 | 0.5 | EI |  | CT_O/G_SIEMENS MCC
0.415kV PIROTEC PCC
6 | I/C PIROTEC PCC (From ETP PCC) | 2000A rating | Schneider | ETA 6G | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.9-0.95-0.98-1 | 0.5-1-2-4-8-12-16-20-24 | 0.4 | 0.5 |  | 0.8 | 1 |  |  | CB_I/C_PIROTEC PCC
[5 empty] | S |  | S/C | 1.5-2-2.5-3-4-5-6-8-10 | 0-0.1-0.2-0.3-0.4 (ms) | 1.5 | 0.1 |  | 4 | 0.4
[5 empty] | I |  | Instantaneous | 2-3-4-6-8-10-12-15 | 0.025 | 2
[5 empty] | G |  | Ground | 500-640-720-800-880-960-1040-1120-1200 | 0-0.1-0.2-0.3-0.4 (ms) | 500 | 0.1 |  | 0.5 | 0.4
7 | I/C PIROTEC PCC (From RO-ZLD PCC) | 800A rating | Schneider | MVS20N ETA 6G | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.9-0.95-0.98-1 | 0.5-1-2-4-8-12-16-20-24 | 0.4 | 0.5 |  | 1 | 0.5 |  |  | CB2_O/G2_PYROTEC PCC
[5 empty] | S |  | S/C | 1.5-2-2.5-3-4-5-6-8-10 | 0-0.1-0.2-0.3-0.4 (ms) | 1.5 | 0.1 |  | 4 | 0.2
[5 empty] | I |  | Instantaneous | 2-3-4-6-8-10-12-15 | 0.025 | 2
[5 empty] | G |  | Ground | 500-640-720-800-880-960-1040-1120-1200 | 0-0.1-0.2-0.3-0.4 (ms) | 500 | 0.1 |  | 0.8 | 0.2
8 | O/G LECHAT MCC | 250A rating | Siemens | MCCB | L |  | O/L | 0.8-0.1-1.0 |  |  |  |  | 1 |  |  | 250 A MCCB | CB1_LECHAT MCC
[5 empty] | I |  | Instantaneous | 5-1-10 | 0.025 | 1 | 0.025 |  | 5 | 0.025
9 | O/G CANEL PUMP MCC | 250A rating | Siemens | MCCB | L |  | O/L | 0.8-0.1-1.0 |  |  |  |  | 1 |  |  | 250 A MCCB | CB_CANEL PUMP MCC
[5 empty] | I |  | Instantaneous | 5-1-10 | 0.025 | 1 | 0.025 |  | 5 | 0.025
10 | O/G BCH MCC | 800A rating | Schneider | MVS20N ETA 6G | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.9-0.95-0.98-1 | 0.5-1-2-4-8-12-16-20-24 | 0.4 | 0.5 |  | 1 | 2 |  |  | CB1_O/G_BCH MCC
[5 empty] | S |  | S/C | 1.5-2-2.5-3-4-5-6-8-10 | 0-0.1-0.2-0.3-0.4 (ms) | 1.5 | 0.1 |  | 5 | 0.2
[5 empty] | I |  | Instantaneous | 2-3-4-6-8-10-12-15 | 0.025 | 2
[5 empty] | G |  | Ground | 500-640-720-800-880-960-1040-1120-1200 | 0-0.1-0.2-0.3-0.4 (ms) | 500 | 0.1 |  | 0.4 | 0.2
11 | O/G HYDRAULIC F/P | 125A rating | Siemens | MCCB | L |  | O/L | 1 |  |  |  |  | 1 |  |  | 125 A MCCB | CB_HYDRAULIC F/P
[5 empty] | I |  | Instantaneous | 1 | 0.025 | 1 | 0.025 |  | 1 | 0.025
0.415kV LECHAT MCC
12 | I/C LECHAT MCC | 250A rating | Siemens | MCCB | L |  | O/L | 0.8-0.1-1.0 |  |  |  |  | 1 |  |  | 250 A MCCB | CB2_LECHAT MCC
[5 empty] | I |  | Instantaneous | 5-1-10 | 0.025 | 1 | 0.025 |  | 5 | 0.025
13 | O/G HRM LECHAT MCC | 38A Rating | Siemens | MPCB 3RV1131/4DA10 SIRIUS | [5 empty] | 21 | [5 empty] | 38A | R_HRM_LECHAT MCC
0.415kV CANEL PUMP MCC
14 | I/C CANEL PUMP MCC | 250A rating | L&T | SFU | [12 empty] | F_I/C_CANEL PUMP MCC
15 | I/C HRM CANEL PUMP MCC | 100A rating | L&T | SFU | [12 empty] | F_HRM_CANEL PUMP MCC
0.415kV BCH MCC
13 | I/C BCH MCC | 2000A rating | SIEMENS | ETU27B Release | L |  | O/L | 0.4-0.45-0.5-0.55-0.6-0.65-0.7-0.8-0.9-1 | 10 (s) | 1 |  |  | 0.5 |  |  |  | CB2_O/G_BCH MCC
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | 0.02-100-200-300-400 (ms) | 6 | 0 |  | 4 | 0.2
[5 empty] | I |  | Instantaneous | 20 | 0.025
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 (ms) |  |  |  | 600 | 200
17 | O/G HRM BCH MCC | 250A rating | L&T | SFU | [12 empty] | F_HRM_BCH MCC
|  | 75A Rating | Siemens | MPCB 3RB21534FW2 SIRIUS | [5 empty] | 75 | [5 empty] | 75A | R_O/G_HRM_BCH MCC
18 | O/G LIME MCC | 80A Rating | Siemens | MPCB 3RV1131/4DA10 SIRIUS | [5 empty] | 80 | [5 empty] | 80A | R_O/G_LIME MCC
0.415kV LIME MCC
19 | I/C LIME MCC | 250A rating | L&T | SFU | [12 empty] | F_LIME MCC
20 | O/G HRM LIME MCC | 50A rating | L&T | SFU | [12 empty] | F_HRM _ LIME MCC
0.415kV EMAC MCC
14 | I/C EMAC MCC | 400A rating | Siemens | MCCB | L |  | O/L | 0.8-0.1-1.0 |  |  |  |  | 1 |  |  | 400 A MCCB | CB_I/C_EMAC MCC
[5 empty] | I |  | Instantaneous | 5-1-10 | 0.025 | 1 | 0.025 |  | 5 | 0.025
22 | O/G HRM EMAC MCC | 63A rating | L&T | SFU | [12 empty] | F_HRM_EMAC MCC
0.415kV SIEMENS MCC
15 | I/C SIEMENS MCC | 1000A rating | MG | MicoLogic 6.0A | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.9-0.95-0.98-1 | 0.5-1-2-4-8-12-16-20-24 | 0.7 | 0.5 |  | 0.7 | 0.5 |  |  | CB_I/C_SIEMENS MCC
[5 empty] | S |  | S/C | 1.5-2-2.5-3-4-5-6-8-10 | 0.1-0.2-0.3-0.4 (s) | 1.5 | 0.1 |  | 5 | 0.2
[5 empty] | I |  | Instantaneous | 2-3-4-6-8-10-12-15-OFF | 0.02 | 2 | -
[5 empty] | G |  | Ground | 0.2-0.3-0.4-0.5-0.6-0.7-0.8-0.9-1.0 | 0.1-0.2-0.3-0.4 (s) | 0.2 | 0.1 |  | 0.2 | 0.1
24 | O/G HRM SIEMENS MCC | 50A Rating | Siemens | MPCB 3RV1131/4DA10 SIRIUS | [5 empty] | 50 | [5 empty] | 50A | CB_O/G_HRM_SIEMENS MCC

## SS-4
SS - 4
Department |  |  | Author |  | Status | [7 empty] | Date |  | Lang.
Power Consulting |  |  | Pritul Panchal |  | Rev A | [7 empty] | 2023-12-28 |  | en
sr. No | FeederType or Location | CT Ratio Amps | Relay Make | Relay Type | Relay NEMA Code | IEC Code | Prot Type | Relay Range |  | Exisitng Setting |  |  | Proposed Setting |  |  | Remark
[8 empty] | Plug setting range | Time setting range (s) / TMs range | Plug setting | Time setting (s) / TMs | Charact eristic | Plug setting | Time setting (s) / TMs | Charact eristic
0.415kV SS - 4
1 | I/C AUX TR 7 Bus-A | 3200A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 0.9 |  |  | 0.9 | - |  |  | CB_O/G_AUX TR 7
[5 empty] | S |  | S/C | 17.5kA & 22kA | 0.025 | - | - |  | - | -
|  | 3200/5 | Alstom | CDG14 | 51N | I0> | EF | 10% .. 320% | 0.1 .. 1.0 | 0.75 | 0.8 | EI | 0.35 | 1 | EI |  | CT_O/G_AUX TR 7
2 | I/C AUX TR-6 Bus-B | 3200A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 0.9 |  |  | 0.9 | - |  |  | CB_O/G_AUX TR-6
[5 empty] | S |  | S/C | 17.5kA & 22kA | 0.025 | - | - |  | - | -
|  | 3200/5 | Alstom | CDG14 | 51N | I0> | EF | 10% .. 320% | 0.1 .. 1.0 | 0.75 | 0.8 | EI | 0.4 | 1 | EI |  | CT_O/G_AUX TR-6
3 | O/G2 R2 LT MCC | 1000A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 1 |  |  | 1 | - |  |  | CB2_O/G2_R2 LT MCC
[5 empty] | S |  | S/C | 5.7kA & 7.2kA | 0.025 | - | - |  | 7.2 | 0.025
|  | 600/5 | Alstom | CDG14 | 51N | I0> | EF | 10% .. 320% | 0.1 .. 1.0 | 0.5 | 0.8 | EI | 0.1 | 0.5 | EI |  | CT_O/G2_R2 LT MCC
4 | O/G MR MCC | 1600A rating | L&T | UW-MTX1.5G | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.85-0.9-0.95-1 | 0.5-1-2-4-6-12-18-24-30 | 1 | 12 |  | 0.7 | 30 |  |  | CB1_O/G_MR MCC
[5 empty] | S |  | S/C | 0.6-1-1.5-2-3-4-6-8-10-12 | 20-100-200-300-400 (ms) | 4 | 0.4 |  | 4 | 0.2
[5 empty] | I |  | Instantaneous | 1.5-2-3-4-6-8-10-12-15 | 0.025 | OFF
[5 empty] | G |  | Ground | 0.2-0.3-0.4-0.5-0.6 | 0.1-0.2-0.3-0.4-1 (s) | 0.6 | 0.1 |  | 0.4 | 0.1
5 | O/G1 TGT PLANT MCC | 3200A rating | Siemens | ETU8WT Release | L |  | O/L | 0.4-0.45-0.5-0.55-0.6-0.65-0.7-0.8-0.9-1 | 10 (s) | 0.4 | 10 |  | 0.4 | 2 |  |  | CB1_O/G1_TGT PLANT MCC
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | 0.02-0.1-0.2-0.3-0.4 (s) | 3 | 0.08 |  | 3 | 0.2
[5 empty] | I |  | Instantaneous | 20 | 0.025 | 15
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 0.1-0.2-0.3-0.4-0.5 (s) | 0.6 | 0.1 |  | 0.6 | 0.1
6 | O/G R2 BLENDE HANDLING MCC EPZ 507 | 800A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 1 |  |  | 0.8 | - |  |  | CB1_I/C_R2 BLENDE HANDLING MCC EPZ 507
[5 empty] | S |  | S/C | 4.7kA & 6kA | 0.025 | - | - |  | 5.7 | 0.025
|  | 800/5 | Alstom | CDG14 | 51N | I0> | EF | 10% .. 320% | 0.1 .. 1.0 | 0.5 | 0.8 | EI | 0.1 | 1 | EI |  | CT_I/C_BLENDE HANDLING MCC EPZ 507
7 | O/G PH 1 NEW MCC 2EPU 505 | 800A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 0.75 |  |  | 1 | - |  |  | CB_O/G_PH 1 SIEMENS & LT MCC
[5 empty] | S |  | S/C | 4.7kA & 6kA | 0.025 | - | - |  | 5.7 | 0.025
|  | 800/5 | Alstom | CDG14 | 51N | I0> | EF | 10% .. 320% | 0.1 .. 1.0 | 0.5 | 0.8 | EI | 0.1 | 1 | EI |  | CT_O/G_PH 1 NEW MCC 2EPU 505
8 | O/G L&P 201B1 MCC | 800A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 1 |  |  | 1 | - |  |  | CB_I/C_L&P 201B1 MCC
[5 empty] | S |  | S/C | 4.7kA & 6kA | 0.025 | - | - |  | 5.7 | 0.025
|  | 800/5 | Alstom | CDG14 | 51N | I0> | EF | 10% .. 320% | 0.1 .. 1.0 | 0.5 | 0.8 | EI | 0.1 | 1 | EI |  | CT_I/C_LEACHING MCC 2EPZ 201B1
9 | O/G1 LEACHING 201B2 MCC | 1000A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 1 |  |  | 1 | - |  |  | CB1_O/G1_LEACHING 201B2 MCC
[5 empty] | S |  | S/C | 5.7kA & 7.2kA | 0.025 | - | - |  | 7.2 | 0.025
|  | 1000/5 | Alstom | CDG14 | 51N | I0> | EF | 10% .. 320% | 0.1 .. 1.0 | 0.5 | 0.8 | EI | 0.1 | 0.2 | EI |  | CT1_I/C_LEACHING MCC 2EPZ 201B2
10 | O/G2 STANDBY CADMIUM 2EPZ 701 (From SS-4 Bus-B) | 800A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 1 |  |  | 1 | - |  |  | CB_O/G2_STANDBY CADMIUM 2EPZ 701 1
[5 empty] | S |  | S/C | 4.7kA & 6kA | 0.025 | - | - |  | 6 | 0.025
11 | O/G PURIFICATION MCC 201A | 1000A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 1 |  |  | 1 | - |  |  | CB1_I/C_PURIFICATION MCC 201A
[5 empty] | S |  | S/C | 5.7kA & 7.2kA | 0.025 | - | - |  | 5.7 | 0.025
|  | 800/5 | Alstom | CDG14 | 51N | I0> | EF | 10% .. 320% | 0.1 .. 1.0 | 0.5 | 0.5 | EI | 0.1 | 0.2 | EI |  | CT_I/C_PURIFICATION MCC 2EPZ 201A
12 | O/G1 M&C GE MCC | 1250A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 1 |  |  | 1 | - |  |  | CB1_O/G1_M&C GE MCC
[5 empty] | S |  | S/C | 7kA & 8.9kA | 0.025 | - | - |  | 7 | 0.025
|  | 800/5 | Universal Electrics Ltd | R1638 | 51N | I0> | EF | 10% .. 320% | 0.1 .. 1.0 | 1 | 0.3 | EI | 0.2 | 0.2 | EI |  | CT_O/G1_M&C GE MCC
13 | O/G1 FILTER WATER MCC PH-1 (From SS-4) | 1000A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 1 |  |  | 1 | - |  |  | CB1_O/G1_FILTER WATER MCC PH-1
[5 empty] | S |  | S/C | 5.7kA & 7.2kA | 0.025 | - | - |  | 5.7 | 0.025
|  | 1000/5 | Alstom | CDG14 | 51N | I0> | EF | 10% .. 320% | 0.1 .. 1.0 | 0.5 | 0.2 | EI | 0.1 | 0.2 | EI |  | CT_O/G1_FILTER WATER MCC PH-1
14 | O/G L&P MCC-2 | 1600A rating | L&T | UW-MTX1.5G | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.85-0.9-0.95-1 | 0.5-1-2-4-6-12-18-24-30 | 1 | 4 |  | 0.5 | 12 |  |  | CB1_O/G_L&P MCC-2
[5 empty] | S |  | S/C | 0.6-1-1.5-2-3-4-6-8-10-12 | 20-100-200-300-400 (ms) | 4 | 0.4 |  | 4 | 0.2
[5 empty] | I |  | Instantaneous | 1.5-2-3-4-6-8-10-12-15 | 0.025 | OFF
[5 empty] | G |  | Ground | 0.2-0.3-0.4-0.5-0.6 | 0.1-0.2-0.3-0.4-1 (s) | 0.4 | 0.1 |  | 0.4 | 0.1
15 | O/G2 PH2 MCC (From SS-4) | 800A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 1 |  |  | 1 | - |  |  | CB1_O/G2_PH2 MCC
[5 empty] | S |  | S/C | 4.7kA & 6kA | 0.025 | - | - |  | 5.7 | 0.025
|  | 800/5 | Alstom | CDG14 | 51N | I0> | EF | 10% .. 320% | 0.1 .. 1.0 | 0.5 | 0.15 | EI | 0.2 | 0.2 | EI |  | CT_O/G_1_NEW MECHING MCC-3
16 | O/G2 PH2 MCC (From SS-4) | 1600A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 1 |  |  | 1 | - |  |  | CB2_O/G_TIE TO SS-5
[5 empty] | S |  | S/C | 8.8kA & 11.5kA | 0.025 | - | - |  | - | -
|  | 1600/5 | English Electric | R1638 | 51N | I0> | EF | 10% .. 320% | 0.1 .. 1.0 | 1 | 0.35 | EI | 0.4 | 0.5 | EI |  | CT2_O/G_TIE TO SS-5
17 | O/G2 PH2 MCC (From SS-4) | 1000A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 0.9 |  |  | 1 | - |  |  | CB_OG2_ ZE 301A MCC (SS-4) 2
[5 empty] | S |  | S/C | 5.7kA & 7.2kA | 0.025 | - | - |  | - | -
|  | 800/5 | Alstom | CDG14 | 51N | I0> | EF | 10% .. 320% | 0.1 .. 1.0 | 0.5 | 0.35 | EI | 0.4 | 0.5 | EI |  | CT_OG2_ ZE 301A MCC (SS-4)
0.415kV MR MCC
18 | I/C MR MCC | 1250A rating | Siemens | ETU37 Release | L |  | O/L | 0.4-0.45-0.5-0.55-0.6-0.65-0.7-0.8-0.9-1 | 10 (s) | 1 | 10 |  | 0.8 |  |  |  | CB2_O/G_MR MCC
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | 0.02-0.1-0.2-0.3-0.4 (s) | 2 | 0.2 |  | 4 | 0.2
[5 empty] | I |  | Instantaneous | 20 | 0.025 | OFF
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 0.1-0.2-0.3-0.4-0.5 (s) | OFF |  |  | 600 | 0.1
19 | O/G HRM MR MCC | 160A rating | Siemens | MCCB | L |  | O/L | 0.8-0.1-1.0 |  |  |  |  | 1 |  |  |  | CB_O/G_HRM_MR MCC
[5 empty] | I |  | Instantaneous | 5-1-10 | 0.025 | 1 | 0.025 |  | 7 | 0.025
0.415kV TGT PLANT MCC
20 | I/C1 TGT PLANT MCC (From SS-4) | 3200A rating | Siemens | ETU8WT Release | L |  | O/L | 0.4-0.45-0.5-0.55-0.6-0.65-0.7-0.8-0.9-1 | 10 (s) | 0.4 | 10 |  | 0.4 | 2 |  |  | CB2_O/G1_TGT PLANT MCC
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | 0.02-0.1-0.2-0.3-0.4 (s) | 3 | 0.08 |  | 3 | 0.2
[5 empty] | I |  | Instantaneous | 20 | 0.025
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 0.1-0.2-0.3-0.4-0.5 (s) | 0.6 | 0.1 |  | 600 | 0.1
21 | O/G TGT PLANT MCC | 100A rating | Siemens | MCCB | L |  | O/L | 1 |  |  |  |  | 1 |  |  |  | CB_O/G_TGT PLANT MCC
[5 empty] | I |  | Instantaneous | 1 | 0.025 | 1 | 0.025 |  | 1 | 0.025
0.415kV R2 BLENDE HANDLING MCC EPZ 507
22 | I/C R2 BLENDE HANDLING MCC EPZ 507 | 250A rating | L&T | SFU | [12 empty] | CB2_I/C_R2 BLENDE HANDLING MCC EPZ 507
22 | O/G BLENDE HANDLING MCC EPZ 507 | 63A rating | Siemens | MCCB | L |  | O/L | 0.8-0.1-1.0 |  |  |  |  | 1
[5 empty] | I |  | Instantaneous | 5-1-10 | 0.025 | 1 | 0.025 |  | 1 | 0.025
0.415kV PH1 SIEMENS MCC
23 | I/C PH1 SIEMENS MCC | 250A rating | Siemens | MCCB | L |  | O/L | 1 |  |  |  |  | 1 |  |  |  | CB_O/G_PH1 SIEMENS MCC
[5 empty] | I |  | Instantaneous | 1 | 0.025 | 1 | 0.025 |  | 10 | 0.025
24 | O/G HRM PH1 SIEMENS MCC |  | Siemens | MPCB SIEMENS | L |  | O/L | 1 | [7 empty] | 80A MPCB | CB_O/G_HRM_PH1 SIEMENS MCC
[5 empty] | I |  | Instantaneous | 1 | 0.025 | 1 | 0.025
0.415kV PH1 L&T MCC
24 | I/C L&T MCC | 400A rating | Siemens | MCCB | L |  | O/L | 0.8-0.1-1.0 |  |  |  |  | 0.8 |  |  |  | CB_O/G_L&T MCC
[5 empty] | I |  | Instantaneous | 5-1-10 | 0.025 | 1 | 0.025 |  | 5 | 0.025
25 | O/G HRM_L&T MCC | 250A rating | Siemens | MCCB | L |  | O/L | 0.8-0.1-1.0 |  |  |  |  | 0.8 |  |  |  | CB_O/G_HRM_L&T MCC
[5 empty] | I |  | Instantaneous | 5-1-10 | 0.025 | 1 | 0.025 |  | 5 | 0.025
0.415kV L&P 201B1 MCC
26 | I/C L&P 201B1 MCC | 630A rating | L&T | SFU | [12 empty] | F_I/C_L&P 201B1 MCC
27 | O/G HRM L&P 201B1 MCC | 800A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 1 |  |  | 0.75 | - |  |  | CB_O/G_HRM_L&P 201B1 MCC
[5 empty] | S |  | S/C | 4.7kA & 6kA | 0.025 | - | - |  | 5.7 | 0.025
0.415kV LEACHING 201B2 MCC
28 | I/C1 LEACHING 201B2 MCC (From SS-4) | 800A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 1 |  |  | 1 | - |  |  | CB2_O/G1_LEACHING 201B2 MCC
[5 empty] | S |  | S/C | 4.7kA & 6kA | 0.025 | - | - |  | 5.7 | 0.025
|  | 800/1 | Alstom | CDG14 | 51N | I0> | EF | 10% .. 320% | 0.1 .. 1.0 | 0.5 | 0.3 | EI | 0.1 | 0.2 | EI |  | CT2_I/C_LEACHING MCC 2EPZ 201B2
29 | I/C2 LEACHING 201B2 MCC (From SS-1) | 800A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 1 |  |  | 1 | - |  |  | CB2_O/G2_LEACHING 201B2 MCC
[5 empty] | S |  | S/C | 4.7kA & 6kA | 0.025 | - | - |  | 5.7 | 0.025
|  | 800/1 | Alstom | CDG14 | 51N | I0> | EF | 10% .. 320% | 0.1 .. 1.0 | 0.5 | 0.3 | EI | 0.5 | 1 | EI |  | CT_O/G2_LEACHING 201B2 MCC
30 | O/G HRM L&P 202B2 MCC | 160A rating | L&T | SFU | [12 empty] | CB_O/G_HRM_L&P 202B2 MCC
0.415kV PURIFICATION MCC 201A
31 | I/C PURIFICATION MCC 201A | 630A rating | Siemens | MCCB | L |  | O/L | 0.8-0.1-1.0 |  |  |  |  | 1 | - |  |  | CB2_I/C_PURIFICATION MCC 201A
[5 empty] | I |  | Instantaneous | 5-1-10 | 0.025 | 1 | 0.025 |  | 5 | 0.025
32 | O/G1 LEACHING MCC 2EPZ 201C (From PURIFICATION MCC 201A) | 250A rating | Siemens | MCCB | L |  | O/L | 0.8-0.1-1.0 |  |  |  |  | 1 | - |  |  | CB1_O/G1_LEACHING MCC 2EPZ 201C
[5 empty] | I |  | Instantaneous | 5-1-10 | 0.025 | 1 | 0.025 |  | 5 | 0.025
33 | O/G HRM PURIFICATION MCC 201A | 40A rating | Schneider | GV3-ME40 MCCB | L |  | O/L | 1 |  |  |  |  | 1 | - |  |  | CB_O/G_HRM_PURIFICATION MCC 201A
[5 empty] | I |  | Instantaneous | 1 | 0.025 | 1 | 0.025 |  | 1 | 0.025
0.415kV M&C GE MCC
34 | I/C1 M&C GE MCC (From SS-4) | 1000A rating | GE | MPACT M-PRO 17 Plus | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.9-1 | Fixed | 1 |  |  | 1 |  |  |  | CB2_O/G1_M&C GE MCC
[5 empty] | S |  | S/C | 1.5-2-3-4-6-8-10-12 | 0.1-0.2-0.4-0.5-0.6-0.8-1.0 (s)
[5 empty] | I |  | Instantaneous | OFF-2-3-4-6-8-10-12 | 0.025
[5 empty] | G |  | Ground | OFF-0.4-0.6-0.8-1 | 0.1-0.2-0.4-0.6-0.8-1.0 (s)
35 | I/C2 M&C GE MCC (From SS-5) | 1000A rating | GE | MPACT M-PRO 17 Plus | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.9-1 | Fixed | 1 |  |  | 1 |  |  |  | CB2_O/G2_M&C GE MCC
[5 empty] | S |  | S/C | 1.5-2-3-4-6-8-10-12 | 0.1-0.2-0.4-0.5-0.6-0.8-1.0 (s)
[5 empty] | I |  | Instantaneous | OFF-2-3-4-6-8-10-12 | 0.025
[5 empty] | G |  | Ground | OFF-0.4-0.6-0.8-1 | 0.1-0.2-0.4-0.6-0.8-1.0 (s)
38 | O/G HRM M&C GE MCC | 250A rating | L&T | SFU | [12 empty] | CB_O/G_HRM_M&C GE MCC
36 | O/G HRM M&C GE MCC | 150/5 | BOCR | 3ez | 50 | I>> | P/F Hs | 15A-180A | 1 .. 30 | 140A | 10 | DT | 140 | 10 | DT |  | CT_O/G_HRM_M&C GE MCC
0.415kV FILTER WATER MCC PH-1
37 | I/C1 FILTER WATER MCC PH-1 (From SS-4) | 400A rating | Siemens | MCCB | L |  | O/L | 0.8-0.1-1.0 |  |  |  |  | 1 | - |  |  | CB2_O/G1_FILTER WATER MCC PH-1
[5 empty] | I |  | Instantaneous | 5-1-10 | 0.025 | 1 | 0.025 |  | 5 | 0.025
38 | O/G HRM FILTER WATER MCC PH-1 | 100A rating | Siemens | MCCB | L |  | O/L | 1 |  |  |  |  | 1 | - |  |  | CB_O/G_HRM_FILTER WATER MCC PH-1
[5 empty] | I |  | Instantaneous | 1 | 0.025 | 1 | 0.025 |  | 1 | 0.025
0.415kV L&P MCC-2
39 | I/C L&P MCC-2 | 1250A rating | Siemens | ETU37 Release | L |  | O/L | 0.4-0.45-0.5-0.55-0.6-0.65-0.7-0.8-0.9-1 | 10 (s) | 1 | 10 |  | 0.4 | 10 |  |  | CB2_O/G_L&P MCC-2
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | 0.02-0.1-0.2-0.3-0.4 (s) | 2 | 0.2 |  | 3 | 0.2
[5 empty] | I |  | Instantaneous | 20 | 0.025 | OFF
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 0.1-0.2-0.3-0.4-0.5 (s) | OFF |  |  | 600 | 0.2
40 | O/G HRM_L&P MCC-2 | 250A rating | Siemens | MCCB | L |  | O/L | 0.8-0.1-1.0 |  | 1 |  |  | 0.8 | - |  |  | CB_O/G_HRM_L&P MCC-2
[5 empty] | I |  | Instantaneous | 5-1-10 | 0.025 | 2000 |  |  | 5 | 0.025
0.415kV LEACHING MCC 2EPZ 201C
41 | I/C1 LEACHING MCC 2EPZ 201C (From PURIFICATION MCC 201A) | 250A rating | Siemens | MCCB | L |  | O/L | 0.8-0.1-1.0 |  | 1 |  |  | 1 | - |  |  | CB2_O/G1_LEACHING MCC 2EPZ 201C
[5 empty] | I |  | Instantaneous | 5-1-10 | 0.025 |  |  |  | 5 | 0.025
42 | I/C2 CADMIUM BUILDING PCC II (From CADMIUM BUILDING PCC II SS-2) | 250A rating | SCHNEIDER | CVS250_TM250D MCCB | L |  | O/L | 0.8-0.1-1.0 |  | 1 |  |  | 1 | - |  |  | CB2_O/G2_CADMIUM BUILDING PCC II
[5 empty] | I |  | Instantaneous | 10 | 0.025 |  |  |  | 10 | 0.025
46 | O/G LEACHING MCC 2EPZ 201C | 100A rating | L&T | SFU | [12 empty] | CB_O/G_LEACHING MCC 2EPZ 201C

## SS-5
SS - 5
Department |  |  | Author |  | Status | [7 empty] | Date |  | Lang.
Power Consulting |  |  | Pritul Panchal |  | Rev A | [7 empty] | 2023-12-28 |  | en
sr. No | FeederType or Location | CT Ratio Amps | Relay Make | Relay Type | Relay NEMA Code | IEC Code | Prot Type | Relay Range |  | Exisitng Setting |  |  | Proposed Setting |  |  | Remark
[8 empty] | Plug setting range | Time setting range (s) / TMs range | Plug setting | Time setting (s) / TMs | Charact eristic | Plug setting | Time setting (s) / TMs | Charact eristic
0.415kV SS - 5
1 | I/C TIE TO SS-5 Bus-A (From SS-4) | 1600A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 1 |  |  | 1 | - |  |  | CB1_O/G_TIE TO SS-5
[5 empty] | S |  | S/C | 8.8kA & 11.5kA | 0.025 | - | - |  | - | -
|  | 1600/5 | English Electric | R1638 | 51N | I0> | EF | 1-1.5-2-2.5-3-3.5-4 | 0.1 .. 1.0 | 1 | 0.8 | EI | 0.4 | 0.5 | EI |  | CT1_O/G_TIE TO SS-5
2 | I/C SS-5 Bus-B RTP TR | 3200A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 0.75 |  |  | 1 | - |  |  | CB_O/G_SS-5_RTP TR
[5 empty] | S |  | S/C | 17.5kA & 22kA | 0.025 | - | - |  | - | -
|  | 3200/5 | Alstom | CDG24 | 51N | I0> | E/F | 10% .. 320% | 0.1 .. 1.0 | 1.5 | 0.5 | EI | 0.2 | 1 | EI
|  | 3200/5 | Alstom | CAG14 | 50N | I0>> | E/F Hs | 20% .. 80% | 0.025 | 0.5 | 0.025 | DT | 0.6 | 0.1 | DT |  | CT_O/G_SS-5_RTP TR
3 | I/C TIE SS-5 & SS 6 Bus-C (From SS-6) | 1600A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 1 |  |  | 1 | - |  |  | CB2_O/G_TIE SS-5 & SS 6
[5 empty] | S |  | S/C | 8.8kA & 11.5kA | 0.025 | - | - |  | - | -
|  | 1600/5 | English Electric | R1638 | 51N | I0> | EF | 1-1.5-2-2.5-3-3.5-4 | 0.1 .. 1.0 | 1 | 1 | EI | 0.2 | 0.5 | EI |  | CT2_O/G_TIE SS-5 & SS 6
4 | O/G SUPPLY TO INTERLAC | 1250A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 1 |  |  | 0.75 | - |  |  | CB1_O/G_SUPPLY TO INTERLAC
[5 empty] | S |  | S/C | 7kA & 8.9kA | 0.025 | - | - |  | - | -
5 | O/G WATER CLEARIFIR | 1250A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 1 |  |  | 0.75 | - |  |  | CB1_O/G_WATER CLEARIFIR
[5 empty] | S |  | S/C | 7kA & 8.9kA | 0.025 | - | - |  | 7 | 0.025
|  | 400/5 | English Electric | R1638 | 51N | I0> | EF | 1-1.5-2-2.5-3-3.5-4 | 0.1 .. 1.0 | 1 | 1 | EI | 0.4 | 0.2 |  |  | CT_O/G_WATER CLEARIFIR
6 | I/C WATER CLEARIFIR | 1250A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 1 |  |  | 0.75 | - |  |  | CB2_O/G_WATER CLEARIFIR
[5 empty] | S |  | S/C | 7kA & 8.9kA | 0.025 | - | - |  | 7 | 0.025
7 | O/G1 LEACHING MCC-1 (From SS-5 Bus-A) | 1250A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 1 |  |  | 0.9 | - |  |  | CB1_O/G_1_LEACHING MCC-1
[5 empty] | S |  | S/C | 7kA & 8.9kA | 0.025 | - | - |  | - | -
|  | 800/5 | English Electric | R1638 | 51N | I0> | EF | 1-1.5-2-2.5-3-3.5-4 | 0.1 .. 1.0 | 2 | 0.6 | EI | 0.2 | 0.2 | EI |  | CT_O/G_1_LEACHING MCC-1
8 | O/G2 M&C GE MCC | 1250A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 1 |  |  | 1 | - |  |  | CB1_O/G2_M&C GE MCC
[5 empty] | S |  | S/C | 7kA & 8.9kA | 0.025 | - | - |  | 7 | 0.025
9 | O/G CAPACITOR CONTROL PANEL | 1250A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 0.75 |  |  | 0.75 | - |  |  | CB1_CAPACITOR CONTROL PANEL
[5 empty] | S |  | S/C | 7kA & 8.9kA | 0.025 | - | - |  | 8.9 | 0.025
|  | 400/5 | English Electric | R1638 | 51N | I0> | EF | 1-1.5-2-2.5-3-3.5-4 | 0.1 .. 1.0 | 1 | 0.1 | EI | 0.4 | 0.2 | EI |  | CT_CAPACITOR CONTROL PANEL
10 | O/G CAP PANEL 1 RHS | 1250A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 1 |  |  | 0.75 | - |  |  | CB1_O/G_CAP PANEL 1 RHS
[5 empty] | S |  | S/C | 7kA & 8.9kA | 0.025 | - | - |  | - | -
|  | 400/5 | English Electric | R1638 | 51N | I0> | EF | 1-1.5-2-2.5-3-3.5-4 | 0.1 .. 1.0 | 1 | 0.1 | EI | 0.4 | 0.2 | EI |  | CT_O/G_CAP PANEL 1 RHS
11 | O/G2 NEW MELTING PCC (STANDBY) | 1250A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 1 |  |  | 1 | - |  |  | CB1_O/G2_NEW MELTING PCC (STANDBY)
[5 empty] | S |  | S/C | 7kA & 8.9kA | 0.025 | - | - |  | - | -
|  | 600/5 | English Electric | R1638 | 51N | I0> | EF | 1-1.5-2-2.5-3-3.5-4 | 0.1 .. 1.0 | 1 | 0.1 | EI | 0.2 | 0.2 | EI |  | CT_O/G2_NEW MELTING PCC (STANDBY)
12 | O/G LT ROOM ADMIN BLOCK | 1250A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 1 |  |  | 0.75 | - |  |  | CB1_O/G_LT ROOM ADMIN BLOCK
[5 empty] | S |  | S/C | 7kA & 8.9kA | 0.025 | - | - |  | 8.9 | 0.025
|  | 600/5 | English Electric | R1638 | 51N | I0> | EF | 1-1.5-2-2.5-3-3.5-4 | 0.1 .. 1.0 | 2 | 0.2 | EI | 0.2 | 0.2 | EI |  | CT_O/G_LT ROOM
13 | I/C LT ROOM ADMIN BLOCK | 250A rating | L&T | SFU | [12 empty] | F_O/G_LT ROOM ADMIN BLOCK
13 | O/G FILTERATION MCC-03 | 1600A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 1 |  |  | 0.75 | - |  |  | CB1_I/C_FILTERATION MCC-03
[5 empty] | S |  | S/C | 8.8kA & 11.5kA | 0.025 | - | - |  | - | -
|  | 800/5 | English Electric | R1638 | 51N | I0> | EF | 1-1.5-2-2.5-3-3.5-4 | 0.1 .. 1.0 | 1 | 0.5 | EI | 0.2 | 0.5 | EI |  | CT_I/C_FILTERATION MCC-03
14 | O/G SULZER MCC | 2000A rating | L&T | UW-MTX1.5G | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.85-0.9-0.95-1 | 0.5-1-2-4-6-12-18-24-30 | 0.8 | 6 |  | 0.4 | 24 |  |  | CB1_O/G_SULZER MCC
[5 empty] | S |  | S/C | 0.6-1-1.5-2-3-4-6-8-10-12 | 20-100-200-300-400 (ms) | 4 | 0.4 |  | 2 | 0.2
[5 empty] | I |  | Instantaneous | 1.5-2-3-4-6-8-10-12-15 | 0.025 | OFF
[5 empty] | G |  | Ground | 0.2-0.3-0.4-0.5-0.6 | 0.1-0.2-0.3-0.4-1 (s) | 0.6 | 1 |  | 0.3 | 0.1
15 | O/G INDUCTION FURNACE PCC SUPPLY | 1250A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 1 |  |  | 0.8 | - |  |  | CB1_O/G_INDUCTION FURNACE PCC SUPPLY
[5 empty] | S |  | S/C | 7kA & 8.9kA | 0.025 | - | - |  | 7 | 0.025
|  | 800/5 | English Electric | R1638 | 51N | I0> | EF | 1-1.5-2-2.5-3-3.5-4 | 0.1 .. 1.0 | 1 | 0.4 | EI | 0.2 | 1 | EI |  | CT1_O/G_INDUCTION FURNACE PCC SUPPLY
0.415kV SUPPLY TO INTERLAC
16 | I/C SUPPLY TO INTERLAC | 2000A rating | Siemens | ETU45B | L |  | O/L | 0.4-0.45-0.5-0.55-0.6-0.65-0.7-0.8-0.9-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 0.8 | 30 |  | 0.4 | 2 |  |  | CB2_O/G_SUPPLY TO INTERLAC
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 | 3 | 400 |  | 1.5 | 200
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20 (ms) | 12
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | OFF |  |  | 300 | 200
17 | O/G HRM SUPPLY TO INTERLAC | 400A rating | Siemens | MCCB | L |  | O/L | 0.8-0.1-1.0 |  | 0.8 |  |  | 0.8 | - |  |  | CB_O/G_HRM_SUPPLY TO INTERLAC
[5 empty] | I |  | Instantaneous | 5-1-10 | 0.025 | 5 | 0.025 |  | 5 | 0.025
0.415kV LEACHING MCC-1
18 | I/C1 LEACHING MCC-1 (From SS-5 Bus-A) | 1000A rating | GE POWER CONTROLS INDIA PVT. LTD. | STATIC RELEASE LMZ 2 | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.9-1.0 | 5-15-40 (s) | 0.9 |  |  | 0.6 | 5 |  |  | CB2_O/G_1_LEACHING MCC-1
[5 empty] | S |  | S/C | 2-3-4-6-8-10 | 50-100-200-300-500 (ms) | 3 | 0.4 |  | 4 | 200
[5 empty] | I |  | Instantaneous | 2-3-5-8-10-OFF | 20 (ms) | - | -
[5 empty] | G |  | Ground | 0.25-0.3-0.4-0.5-0.6-0.7 | 200-300-400 (ms) | 0.3 | 0.6 |  | 0.3 | 200
19 | I/C2 LEACHING MCC-1 (From SS-5 Bus-C) | 1000A rating | GE POWER CONTROLS INDIA PVT. LTD. | STATIC RELEASE LMZ 2 | L |  | O/L | 0.4-0.5-0.6-0.7-0.8-0.9-1.0 | 5-15-40 (s) | 0.9 |  |  | 0.6 | 5 |  |  | CB2_O/G_2_LEACHING MCC-1
[5 empty] | S |  | S/C | 2-3-4-6-8-10 | 50-100-200-300-500 (ms) | 3 | 0.4 |  | 4 | 200
[5 empty] | I |  | Instantaneous | 2-3-5-8-10-OFF | 20 (ms) | - | -
[5 empty] | G |  | Ground | 0.25-0.3-0.4-0.5-0.6-0.7 | 200-300-400 (ms) | 0.3 | 0.6 |  | 0.3 | 200
0.415kV CAPACITOR CONTROL PANEL (LHS)
20 | I/C CAPACITOR CONTROL PANEL | 250A rating | Siemens | MCCB | L |  | O/L | 0.8-0.1-1.0 |  | 0.8 |  |  | 1 |  |  |  | CB2_CAPACITOR CONTROL PANEL
[5 empty] | I |  | Instantaneous | 5-1-10 | 0.025 | 5 | 0.025 |  | 10 | 0.025
0.415kV CAPACITOR CONTROL PANEL (RHS)
21 | I/C CAPACITOR CONTROL PANEL | 250A rating | Siemens | MCCB | L |  | O/L | 0.8-0.1-1.0 |  | 0.8 |  |  | 1 |  |  |  | CB2_O/G_CAP PANEL 1 RHS
[5 empty] | I |  | Instantaneous | 5-1-10 | 0.025 | 5 | 0.025 |  | 10 | 0.025
0.415kV FILTERATION MCC-03
22 | I/C FILTERATION MCC-03 | 1000A rating | Siemens | ETU45B | L |  | O/L | 0.4-0.45-0.5-0.55-0.6-0.65-0.7-0.8-0.9-1 | 2-3.5-5.5-8-10-14-17-21-25-30 | 0.4 | 2 |  | 0.4 | 2 |  |  | CB2_I/C_FILTERATION MCC-03
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 | 1.25 | 0.1 |  | 3 | 0.2
[5 empty] | I |  | Instantaneous | 1.5-2.2-3-4-6-8-10-12 | 20 (ms) | 12
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 100-200-300-400-500 | 100A | 0.1 |  | 600 | 200
23 | O/G HRM FILTERATION MCC-03 | 400A rating | SCHNEIDER | NX400N MCCB | L |  | O/L | 0.16-0.18-0.2-0.25-0.28-0.32-0.36-0.4 |  | 0.25 |  |  | 0.25 |  |  |  | CB_O/G_HRM_FILTERATION MCC-03
[5 empty] | I |  | Instantaneous | 0.6-1.5-2.4-3-4.8-6.9 | 0.01-0.05 (s) |  |  |  | 5 | 0.02
0.415kV SULZER MCC
24 | I/C SULZER MCC | 1600A rating | Siemens | ETU37 Release | L |  | O/L | 0.4-0.45-0.5-0.55-0.6-0.65-0.7-0.8-0.9-1 | 10 (s) | 1 | 10 |  | 0.4 |  |  |  | CB2_O/G_SULZER MCC
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | 0.02-0.1-0.2-0.3-0.4 (s) | 2 | 0 |  | 2.5 | 0.2
[5 empty] | I |  | Instantaneous | 20 | 0.025 | OFF |  |  | OFF
[5 empty] | G |  | Ground | 100-300-600-900-1200 | 0.1-0.2-0.3-0.4-0.5 (s) | OFF |  |  | 0.6 | 0.2
25 | O/G HRM SULZER MCC | 250A rating | Siemens | MCCB | L |  | O/L | 0.8-0.1-1.0 |  | 1 |  |  | 0.8 |  |  |  | CB_O/G_HRM_SULZER MCC
[5 empty] | I |  | Instantaneous | 5-1-10 | 0.025 | 8 | 0.025 |  | 5 | 0.025
0.415kV INDUCTION FURNACE PCC SUPPLY
26 | I/C1 INDUCTION FURNACE PCC SUPPLY (From SS-5) | 800/5 | CDG31 | Alstom | 51 | I> | P/F | 0.5-0.25-2 | 0.0-0.01-1 | 3.75 | 1 | NI | 1 | 1 | NI |  | CT2_O/G_INDUCTION FURNACE PCC SUPPLY
[5 empty] | 51N | I0> | E/F | 0.1-0.05-0.4 | 0.0-0.01-1 | 1 | 1 | NI | 0.2 | 0.1 | NI
27 | I/C2 INDUCTION FURNACE (STANDBY) (From SS-6) | 800/5 | CDG31 | Alstom | 51 | I> | P/F | 0.5-0.25-2 | 0.0-0.01-1 | 3.75 | 1 | NI | 1 | 1 | NI |  | CT2_O/G_ INDUCTION FURNACE (STANDBY)
[5 empty] | 51N | I0> | E/F | 0.1-0.05-0.4 | 0.0-0.01-1 | 1 | 1 | NI | 0.2 | 0.1 | NI
28 | O/G HRM INDUCTION FURNACE PCC SUPPLY | 800/5 | CDG31 | Alstom | 51 | I> | P/F | 0.5-0.25-2 | 0.0-0.01-1 | 3.75 | 1 | NI | 1 | 1 | NI |  | CT_O/G_HRM_INDUCTION FURNACE PCC SUPPLY
[5 empty] | 51N | I0> | E/F | 0.1-0.05-0.4 | 0.0-0.01-1 | 1.5 | 1 | NI | 0.2 | 0.2 | NI
29 | I/C HRM INDUCTION FURNACE PCC SUPPLY | 1250A rating | Siemens | MCCB | L |  | O/L | 0.4;0.45;0.5;0.6;0.63;0.7;0.8;0.9;0.95;1 | 2.5;4-2-10;14;17;20;25;30 | 1 |  |  | 0.7 | 2.5 |  |  | CB2_O/G_HRM_INDUCTION FURNACE PCC SUPPLY
[5 empty] | I |  | Instantaneous | 1.25;1.5;2-1-6;8;10;11 | 0.025 | 8 | 0.025 |  | 5 | 0.025

## SS-6
SS - 6
Department |  |  | Author |  | Status | [7 empty] | Date |  | Lang.
Power Consulting |  |  | Pritul Panchal |  | Rev A | [7 empty] | 2023-12-28 |  | en
sr. No | FeederType or Location | CT Ratio Amps | Relay Make | Relay Type | Relay NEMA Code | IEC Code | Prot Type | Relay Range |  | Exisitng Setting |  |  | Proposed Setting |  |  | Remark
[8 empty] | Plug setting range | Time setting range (s) / TMs range | Plug setting | Time setting (s) / TMs | Charact eristic | Plug setting | Time setting (s) / TMs | Charact eristic
0.415kV SS - 6
1 | I/C AUX TR 1 | 2000A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 0.8 |  |  | 0.75 | - |  |  | CB_O/G_AUX TR 1
[5 empty] | S |  | S/C | 11kA & 14kA | 0.025 | - | - |  | - | -
|  | 400/5 | Alstom | CDG14 | 51N | I0> | EF | 10% .. 320% | 0.1 .. 1.0 | - | - | EI | 0.45 | 1 | VI | Relay Bypassed | CT_O/G_AUX TR 1
2 | O/G SS 1 | 3200A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 1 |  |  | 1 | - |  |  | CB2_O/G_TO SS 1
[5 empty] | S |  | S/C | 17.5kA & 22kA | 0.025 | - | - |  | - | -
|  | 400/5 | English Electric | R1638 | 51N | I0> | EF | 1-1.5-2-2.5-3-3.5-4 | 0.1 .. 1.0 | 1 | 1 | EI | 0.4 | 1 | VI |  | CT_O/G_TO SS 1
3 | O/G TIE SS-5 & SS 6 (To SS-5) | 1600A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 1 |  |  | 1 | - |  |  | CB1_O/G_TIE SS-5 & SS 6
[5 empty] | S |  | S/C | 8.8kA & 11.5kA | 0.025 | - | - |  | - | -
|  | 400/5 | English Electric | R1638 | 51N | I0> | EF | 1-1.5-2-2.5-3-3.5-4 | 0.1 .. 1.0 | 1 | 1 | EI | 0.2 | 1 | VI |  | CT1_O/G_TIE SS-5 & SS 6
4 | O/G SS-7 PCC | 1250A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 1 |  |  | 1 | - |  |  | CB1_O/G_SS-7 PCC
[5 empty] | S |  | S/C | 7kA & 8.9kA | 0.025 | - | - |  | - | -
|  | 400/5 | English Electric | R1638 | 51N | I0> | EF | 1-1.5-2-2.5-3-3.5-4 | 0.1 .. 1.0 | 1 | 1 | EI | 0.2 | 0.5 | VI |  | CT1_O/G_SS-7 PCC
5 | O/G INDUCTION FURNACE (STANDBY) | 1250A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 0.9 |  |  | 0.9 | - |  |  | CB1_O/G_ INDUCTION FURNACE (STANDBY)
[5 empty] | S |  | S/C | 7kA & 8.9kA | 0.025 | - | - |  | - | -
|  | 400/5 | English Electric | R1638 | 51N | I0> | EF | 1-1.5-2-2.5-3-3.5-4 | 0.1 .. 1.0 | 1 | 0.2 | EI | 0.2 | 1 | VI |  | CT1_O/G_INDUCTION FURNACE PCC (STANDBY)

## SS-7
SS - 7
Department |  |  | Author |  | Status | [7 empty] | Date |  | Lang.
Power Consulting |  |  | Pritul Panchal |  | Rev A | [7 empty] | 2023-12-28 |  | en
sr. No | FeederType or Location | CT Ratio Amps | Relay Make | Relay Type | Relay NEMA Code | IEC Code | Prot Type | Relay Range |  | Exisitng Setting |  |  | Proposed Setting |  |  | Remark
[8 empty] | Plug setting range | Time setting range (s) / TMs range | Plug setting | Time setting (s) / TMs | Charact eristic | Plug setting | Time setting (s) / TMs | Charact eristic
0.415kV SS - 7
1 | I/C SS-7 (From SS-2) | 1250A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 1 |  |  | 1 | - |  |  | CB2_O/G_SS-7 MV SG 7 SY-22712
[5 empty] | S |  | S/C | 7kA & 8.9kA | 0.025 |  |  |  | - | -
|  | 1250/5 | English Electric | R1638 | 51N | I0> | EF | 1-1.5-2-2.5-3-3.5-4 | 0.1 .. 1.0 | 2 | 0.15 | EI | 0.4 | 0.2 | VI |  | CT2_O/G_SS-7 MV SG 7 SY-22712
2 | I/C SS-7 (From SS-6) | 1250A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 1 |  |  | 1 | - |  |  | CB2_O/G_SS-7 PCC
[5 empty] | S |  | S/C | 7kA & 8.9kA | 0.025 |  |  |  | - | -
|  | 1250/5 | English Electric | R1638 | 51N | I0> | EF | 1-1.5-2-2.5-3-3.5-4 | 0.1 .. 1.0 | 2 | 0.25 | EI | 0.4 | 0.2 | VI |  | CT_O/G_SS-7 PCC
3 | O/G ODPH MCC | 1250A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 1 |  |  | 0.75 | - |  |  | CB1_L_ODPH MCC
[5 empty] | S |  | S/C | 7kA & 8.9kA | 0.025 |  |  |  | 7 | 0.025
|  | 1250/5 | English Electric | R1638 | 51N | I0> | EF | 1-1.5-2-2.5-3-3.5-4 | 0.1 .. 1.0 | 2 | 0.25 | EI | 0.2 | 0.2 | VI |  | CT1_L_ODPH MCC
4 | I/C ODPH MCC | 250A rating | L&T | SFU | [12 empty] | F_L_ODPH MCC
4 | O/G2 PH NO 3 MCC | 1250A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 0.9 |  |  | 0.9 | - |  |  | CB1_O/G2_PH NO 3 MCC
[5 empty] | S |  | S/C | 7kA & 8.9kA | 0.025 |  |  |  | 7 | 0.025
|  | 1250/5 | EASUN ROYROLLE | TJM20 | 51N | I0> | EF | 10% .. 40% | 0.1 .. 1.0 | 90% | 0.2 | EI | 0.2 | 0.2 | VI |  | CT1_O/G2_PH NO 3 MCC
5 | O/G RO PLANT MCC | 1250A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 0.9 |  |  | 0.75 | - |  |  | CB1_I/C_RO PLANT MCC
[5 empty] | S |  | S/C | 7kA & 8.9kA | 0.025 |  |  |  | 7 | 0.025
|  | 400/5 | English Electric | R1638 | 51N | I0> | EF | 1-1.5-2-2.5-3-3.5-4 | 0.1 .. 1.0 | 2 | 1 | EI | 0.2 | 0.2 | VI |  | CT1_I/C_RO PLANT MCC
6 | O/G BOILER MCC + HEATER SUPPLY FOR FO | 1250A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 1 |  |  | 0.75 | - |  |  | CB1_I/C_BOILER MCC + HEATER SUPPLY FOR FO
[5 empty] | S |  | S/C | 7kA & 8.9kA | 0.025 |  |  |  | 7 | 0.025
|  | 400/5 | English Electric | R1638 | 51N | I0> | EF | 1-1.5-2-2.5-3-3.5-4 | 0.1 .. 1.0 | 2 | 0.2 | EI | 0.2 | 0.2 | VI |  | CT1_I/C_BOILER MCC + HEATER SUPPLY FOR FO
7 | O/G2 DM NEW MCC-1 | 1250A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 1 |  |  | 0.75 | - |  |  | CB_O/G2_DM NEW MCC-1 1
[5 empty] | S |  | S/C | 7kA & 8.9kA | 0.025 |  |  |  | 7 | 0.025
8 | O/G DM PLANT MCC-3 | 1250A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 0.75 |  |  | 0.75 | - |  |  | CB1_O/G_DM PLANT MCC-3
[5 empty] | S |  | S/C | 7kA & 8.9kA | 0.025 | - | - |  | 7 | 0.025
|  | 1250/5 | English Electric | R1638 | 51N | I0> | EF | 1-1.5-2-2.5-3-3.5-4 | 0.1 .. 1.0 | 1 | 0.15 | EI | 0.2 | 0.2 | EI |  | CT_O/G_DM PLANT MCC-3
0.415kV PH NO 3 MCC
9 | I/C1 PH NO 3 MCC (From PHE PCC) | 1250A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 0.9 |  |  | 0.9 | - |  |  | CB2_O/G1_PH NO 3 MCC
[5 empty] | S |  | S/C | 7kA & 8.9kA | 0.025 |  |  |  | 7 | 0.025
|  | 1250/5 | EASUN ROYROLLE | TJM20 | 51N | I0> | EF | 10% .. 40% | 0.1 .. 1.0 | 90% | 0.2 | EI | 0.2 | 0.2 | VI |  | CT2_I/C_PH NO 3 MCC
10 | I/C2 PH NO 3 MCC (From SS-7) | 1250A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 0.9 |  |  | 0.9 | - |  |  | CB2_O/G2_PH NO 3 MCC
[5 empty] | S |  | S/C | 7kA & 8.9kA | 0.025 |  |  |  | 7 | 0.025
|  | 1250/5 | EASUN ROYROLLE | TJM20 | 51N | I0> | EF | 10% .. 40% | 0.1 .. 1.0 | 90% | 0.2 | EI | 0.2 | 0.2 | VI |  | CT2_O/G2_PH NO 3 MCC
11 | O/G PH NO 3 MCC | 250A rating | Siemens | MCCB | L |  | O/L | 0.8-0.1-1.0 |  |  |  |  | 1 |  |  |  | CB_O/G_PH NO 3 MCC
[5 empty] | I |  | Instantaneous | 5-1-10 | 0.025 | 1 | 10 |  | 10 | 10
0.415kV RO PLANT MCC
13 | I/C RO PLANT MCC | 400A rating | L&T | SFU | [12 empty] | F_I/C_RO PLANT MCC
0.415kV BOILER MCC + HEATER SUPPLY FOR FO
12 | I/C BOILER MCC + HEATER SUPPLY FOR FO | 125A rating | Siemens | MCCB | L |  | O/L | 1 |  |  |  |  | 1 |  |  |  | CB2_I/C_BOILER MCC + HEATER SUPPLY FOR FO
[5 empty] | I |  | Instantaneous | 1 | 0.025 | 1 | 0.025 |  | 1 | 0.025
0.415kV DM PLANT MCC-3
13 | I/C2 DM PLANT MCC-3 (From SS-7) | 630A rating | Siemens | MCCB | L |  | O/L | 0.8-0.1-1.0 |  |  |  |  | 1 |  |  |  | CB2_O/G_DM PLANT MCC-3
[5 empty] | I |  | Instantaneous | 5-1-10 | 0.025 | 1 | 0.025 |  | 5 | 0.025
14 | I/C1 DM PLANT MCC-3 (From PHE PCC) | 630A rating | Siemens | MCCB | L |  | O/L | 0.8-0.1-1.0 |  |  |  |  | 1 |  |  |  | CB2_O/G1_DM PLANT MCC-3
[5 empty] | I |  | Instantaneous | 5-1-10 | 0.025 | 1 | 0.025 |  | 5 | 0.025
15 | O/G HRM DM PLANT MCC-3 | 1000A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 0.75 |  |  | 0.75 | - |  |  | CB_O/G_HRM_DM PLANT MCC-3
[5 empty] | S |  | S/C | 5.7kA & 7.2kA | 0.025 | - | - |  | 5.7 | 0.025

## MELTING FURNACE PCC (hidden)
MELTING FURNACE
Department |  |  | Author |  | Status | [7 empty] | Date |  | Lang.
Power Consulting |  |  | Pritul Panchal |  | Rev A | [7 empty] | 2023-12-28 |  | en
sr. No | FeederType or Location | CT Ratio Amps | Relay Make | Relay Type | Relay NEMA Code | IEC Code | Prot Type | Relay Range |  | Exisitng Setting |  |  | Proposed Setting |  |  | Remark
[8 empty] | Plug setting range | Time setting range (s) / TMs range | Plug setting | Time setting (s) / TMs | Charact eristic | Plug setting | Time setting (s) / TMs | Charact eristic
0.415kV MELTING FURNACE
1 | I/C MELTING FURNACE PCC (From ZN MELT TR) | 3200A rating | Siemens | ETU27B | L |  | O/L | 0.4-0.45-0.5-0.55-0.6-0.65-0.7-0.8-0.9-1 | 10 (s) | 1 | 10 |  | 1 | 6 |  |  | CB_I/C_DEMAG FURNACE
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 (ms) | 6 | 0.4 |  | 6 | 400
[5 empty] | I |  | Instantaneous | 20 | 20 (ms) | 20
[5 empty] | G |  | Ground
2 | I/C MELTING FURNACE PCC (From SS-5) | 3200A rating | Siemens | ETU27B | L |  | O/L | 0.4-0.45-0.5-0.55-0.6-0.65-0.7-0.8-0.9-1 | 10 (s) | 1 | 10 |  | 0.7 |  |  |  | CB2_O/G2_NEW MELTING PCC (STANDBY)
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 (ms) | 6 | 0.4 |  | 4 | 400
[5 empty] | I |  | Instantaneous | 20 | 20 (ms) | 20
[5 empty] | G |  | Ground
3 | O/G DEMAG FURNACE | 1600A rating | Siemens | ETU27B | L |  | O/L | 0.4-0.45-0.5-0.55-0.6-0.65-0.7-0.8-0.9-1 | 10 (s) | 1 | 10 |  | 0.65 |  |  |  | CB1_O/G_DEMAG FURNACE
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 (ms) | 3 | 0.4 |  | 4 | 200
[5 empty] | I |  | Instantaneous | 20 | 20 (ms) | 20
[5 empty] | G |  | Ground
4 | I/C DEMAG FURNACE | 1200A rating | Siemens | MCCB | L |  | O/L | 0.4;0.45;0.5;0.6;0.63;0.7;0.8;0.9;0.95;1 | 2.5;4-2-10;14;17;20;25;30 |  |  |  | 0.9 | 2.5 |  |  | CB2_O/G_DEMAG FURNACE
[5 empty] | I |  | Instantaneous | 1.25;1.5;2-1-6;8;10;11 | 0.025 | 1 | 0.025 |  | 5 | 0.025
5 | O/G AJAX FURNACE | 1600A rating | Siemens | ETU27B | L |  | O/L | 0.4-0.45-0.5-0.55-0.6-0.65-0.7-0.8-0.9-1 | 10 (s) | 0.5 | 10 |  | 0.65 |  |  |  | CB1_O/G_AJAX FURNACE
[5 empty] | S |  | S/C | 1.25-1.5-2-2.5-3-4-6-8-10-12 | M-100-200-300-400 (ms) | 2 | 0.1 |  | 4 | 200
[5 empty] | I |  | Instantaneous | 20 | 20 (ms) | 20
[5 empty] | G |  | Ground
6 | I/C AJAX FURNACE | 1200A rating | Siemens | MCCB | L |  | O/L | 0.4;0.45;0.5;0.6;0.63;0.7;0.8;0.9;0.95;1 | 2.5;4-2-10;14;17;20;25;30 |  |  |  | 0.9 | 2.5 |  |  | CB2_O/G_AJAX FURNACE
[5 empty] | I |  | Instantaneous | 1.25;1.5;2-1-6;8;10;11 | 0.025 | 1 | 0.025 |  | 4 | 0.025
7 | O/G FURNACE BAG FILTER PNL | 250A rating | Siemens | MCCB | L |  | O/L | 0.8-0.1-1.0 |  |  |  |  | 1 |  |  |  | CB1_O/G_FURNACE BAG FILTER PNL
[5 empty] | I |  | Instantaneous | 5-1-10 | 0.025 | 1 | 0.025 |  | 5 | 0.025
0.415kV FURNACE BAG FILTER PNL
8 | I/C FURNACE BAG FILTER PNL | 250A rating | Siemens | MCCB | L |  | O/L | 0.8-0.1-1.0 |  |  |  |  | 1 |  |  |  | CB2_O/G_FURNACE BAG FILTER PNL
[5 empty] | I |  | Instantaneous | 5-1-10 | 0.025 | 1 | 0.025 |  | 5 | 0.025
9 | O/G DEMAG FURNACE BAG FILTER BLOWER | 36A rating | Siemens | MCCB | L |  | O/L | 1 | [8 empty] | R_DEMAG FURNACE BAG FILTER BLOWER
[5 empty] | I |  | Instantaneous | 1 | 0.025 | 1 | 0.025
10 | O/G AJAX BACK FILTER BLOWER | 36A rating | Siemens | MPCB | L |  | O/L | 1 | [8 empty] | R_AJAX BACK FILTER BLOWER
[5 empty] | I |  | Instantaneous | 1 | 0.025 | 1 | 0.025
11 | O/G INDUCTION FURNACE BACK FILTER BLOWER | 40A rating | Siemens | MPCB | L |  | O/L | 1 | [8 empty] | R_INDUCTION FURNACE BACK FILTER BLOWER
[5 empty] | I |  | Instantaneous | 1 | 0.025 | 1 | 0.025

## 11kV Andrew Yule (hidden)
11kV ANDREW YULE PANEL
Department |  |  | Author |  | Status | [7 empty] | Date |  | Lang.
Power Consulting |  |  | Pritul Panchal |  | Rev A | [7 empty] | 2023-12-28 |  | en
sr. No | FeederType or Location | CT Ratio Amps | Relay Make | Relay Type | Relay NEMA Code | IEC Code | Prot Type | Relay Range |  | Exisitng Setting |  |  | Proposed Setting |  |  | Remark
[8 empty] | Plug setting range | Time setting range (s) / TMs range | Plug setting | Time setting (s) / TMs | Charact eristic | Plug setting | Time setting (s) / TMs | Charact eristic
11kV Andrew Yule Bus - A
1 | I/C-1 Andrew Yule Panel (From 11kV Bus - B) | 400/5 | Siemens | 7SR1103 | 51 | I> | P/F | 0.05, 0.06 .. 2.5 | 0.025, 0.030 .. 1.6 | 0.95 | 1 |  | 1.25 | 1 | EI |  | CT2_O/G_1_ANDREW YULE (VCB PNL BRD)
[5 empty] | 50 | I>> | P/F Hs | 0.05, 0.06 .. 2.5, 2.55 .. 50 | 0.00, 0.01 .. 20.00, 20.10 .. 100, 101 .. 1000, 1010 .. 10000, 10100 .. 14400 (s) | 0.8 | 0 |  | 5 | 0.4 | DT
[5 empty] | 51N | I0> | EF | 0.05, 0.06 .. 2.5 | 0.025, 0.030 .. 1.6 | 0.7 | 1 |  | 0.17 | 0.03 | EI
[5 empty] | 50N | I0>> | E/F Hs | 0.05, 0.06 .. 2.5, 2.55 .. 50 | 0.00, 0.01 .. 20.00, 20.10 .. 100, 101 .. 1000, 1010 .. 10000, 10100 .. 14400 (s) | OFF | OFF |  | 0.25 | 0.4 | DT
2 | O/G MCTP TR-5 | 100/5 | CDG31 | Alstom | 51 | I> | P/F | 0.5-0.25-2 | 0.0-0.01-1 | 50A | 0.1 | [5 empty] | CT_I/C_MCTP TR-5
[5 empty] | 51N | I0> | E/F | 0.1-0.05-0.4 | 0.0-0.01-1 | 20A | 0.02
|  |  | ABB | REF615 | 51 | I> | P/F | 0.05-0.01-5.00 | 0.025-0.005-15.000 |  |  |  | 1.2 | 1.07 | EI
[5 empty] | 50 | I>> | P/F Hs | 0.010-0.005-5.000 | 0.025-0.005-15.000 |  |  |  | 18.1 | 0.05 | DT
[5 empty] | 51N | I0> | EF | 0.1-0.01-40.00 | 40-10-200000 (ms) |  |  |  | 0.2 | 0.25 | EI
[5 empty] | 50N | I0>> | E/F Hs | 0.1-0.01-40.00 | 40-10-200000 (ms) |  |  |  | 0.5 | 0.05 | DT
3 | O/G SS-1 TR-1 | 50/5 | CDG31 | Alstom | 51 | I> | P/F | 0.5-0.25-2 | 0.0-0.01-1 | 37.5A | 0.2 | [5 empty] | CT_I/C_SS-1_TR-1
[5 empty] | 51N | I0> | E/F | 0.1-0.05-0.4 | 0.0-0.01-1 | 10A | 0.1
|  |  | ABB | REF615 | 51 | I> | P/F | 0.05-0.01-5.00 | 0.025-0.005-15.000 |  |  |  | 2.26 | 0.8 | EI
[5 empty] | 50 | I>> | P/F Hs | 0.010-0.005-5.000 | 0.025-0.005-15.000 |  |  |  | 35.9 | 0.05 | DT
[5 empty] | 51N | I0> | EF | 0.1-0.01-40.00 | 40-10-200000 (ms) |  |  |  | 0.2 | 0.86 | EI
[5 empty] | 50N | I0>> | E/F Hs | 0.1-0.01-40.00 | 40-10-200000 (ms)
4 | O/G TR (From Andrew Yule) | 300/5 | CDG31 | Alstom | 51 | I> | P/F | 0.5-0.25-2 | 0.0-0.01-1 | 225A | 0.05 | [5 empty] | CT_I/C_TR_ANDREW SPARE
[5 empty] | 51N | I0> | E/F | 0.1-0.05-0.4 | 0.0-0.01-1 | 60A | 0.2
|  |  | ABB | REF615 | 51 | I> | P/F | 0.05-0.01-5.00 | 0.025-0.005-15.000 |  |  |  | 1.05 | 0.2 | NI
[5 empty] | 50 | I>> | P/F Hs | 0.010-0.005-5.000 | 0.025-0.005-15.000 |  |  |  | 4 | 0.05 | DT
[5 empty] | 51N | I0> | EF | 0.1-0.01-40.00 | 40-10-200000 (ms) |  |  |  | 0.2 | 0.2 | NI
[5 empty] | 50N | I0>> | E/F Hs | 0.1-0.01-40.00 | 40-10-200000 (ms) |  |  |  | 0.5 | 0.05 | DT
5 | O/G AUX TR-3 (From Andrew Yule) | 100/5 | CDG31 | Alstom | 51 | I> | P/F | 0.5-0.25-2 | 0.0-0.01-1 | 75A | 0.1 | [5 empty] | CT_I/C_AUX TR-3_ANDREW SPARE
[5 empty] | 51N | I0> | E/F | 0.1-0.05-0.4 | 0.0-0.01-1 | 20A | 0.2
|  |  | ABB | REF615 | 51 | I> | P/F | 0.05-0.01-5.00 | 0.025-0.005-15.000 |  |  |  | 1.15 | 0.9 | EI
[5 empty] | 50 | I>> | P/F Hs | 0.010-0.005-5.000 | 0.025-0.005-15.000 |  |  |  | 20.4 | 0.05 | DT
[5 empty] | 51N | I0> | EF | 0.1-0.01-40.00 | 40-10-200000 (ms) |  |  |  | 0.2 | 0.2 | EI
[5 empty] | 50N | I0>> | E/F Hs | 0.1-0.01-40.00 | 40-10-200000 (ms) |  |  |  | 0.5 | 0.05 | DT
6 | O/G CAP FDR-3 | 300/5 | CDG31 | Alstom | 51 | I> | P/F | 0.5-0.25-2 | 0.0-0.01-1 | 225A | 0.05 |  | 1 | 0.06 | NI |  | CT_O/G_CAP FDR-3
[5 empty] | 51N | I0> | E/F | 0.1-0.05-0.4 | 0.0-0.01-1 | 60A | 0.02 |  | 0.2 | 0.1 | NI
11kV Andrew Yule Bus - B
7 | I/C-2 Andrew Yule Panel (From 11kV Bus - C) | 800/5 | Siemens | 7SR1103 | 51 | I> | P/F | 0.05, 0.06 .. 2.5 | 0.025, 0.030 .. 1.6 | 0.75 | 1 |  | 0.63 | 1.6 | EI |  | CT2_O/G_2_ANDREW YULE (VCB PNL BRD)
[5 empty] | 50 | I>> | P/F Hs | 0.05, 0.06 .. 2.5, 2.55 .. 50 | 0.00, 0.01 .. 20.00, 20.10 .. 100, 101 .. 1000, 1010 .. 10000, 10100 .. 14400 (s) | 0.8 | 0.1 |  | 5 | 0.4 | DT
[5 empty] | 51N | I0> | EF | 0.05, 0.06 .. 2.5 | 0.025, 0.030 .. 1.6 | 0.5 | 0.8 |  | 0.2 | 1.6 | EI
[5 empty] | 50N | I0>> | E/F Hs | 0.05, 0.06 .. 2.5, 2.55 .. 50 | 0.00, 0.01 .. 20.00, 20.10 .. 100, 101 .. 1000, 1010 .. 10000, 10100 .. 14400 (s) | 0.2 | 0.05 |  | 0.5 | 0.4 | DT
8 | O/G CAP FDR-1 | 300/5 | Alstom | CDG31 | 51 | I> | P/F | 0.5-0.25-2 | 0.0-0.01-1 | 225A | 0.05 |  | 1 | 0.05 | NI |  | CT_O/G_CAP FDR-1
[5 empty] | 51N | I0> | E/F | 0.1-0.05-0.4 | 0.0-0.01-1 | 60A | 0.05 |  | 0.2 | 0.1 | NI
9 | O/G DARIBA PUPING STATION | 50/5 | Alstom | CDG31 | 51 | I> | P/F | 0.5-0.25-2 | 0.0-0.01-1 | 37.5A | 1 | [5 empty] | CT_O/G_DARIBA PUPING STATION
[5 empty] | 51N | I0> | E/F | 0.1-0.05-0.4 | 0.0-0.01-1 | 10A | 0
|  |  | ABB | REF615 | 51 | I> | P/F | 0.05-0.01-5.00 | 0.025-0.005-15.000 |  |  |  | 0.94 | 0.2 | NI
[5 empty] | 50 | I>> | P/F Hs | 0.010-0.005-5.000 | 0.025-0.005-15.000 |  |  |  | 20.6 | 0.05 | DT
[5 empty] | 51N | I0> | EF | 0.1-0.01-40.00 | 40-10-200000 (ms) |  |  |  | 0.2 | 0.2 | NI
[5 empty] | 50N | I0>> | E/F Hs | 0.1-0.01-40.00 | 40-10-200000 (ms) |  |  |  | 0.5 | 0.05 | DT
10 | O/G ETP TR | 50/5 | Alstom | CDG31 | 51 | I> | P/F | 0.5-0.25-2 | 0.0-0.01-1 | 37.5A | 0.2 | [5 empty] | CT_I/C_ETP TR
[5 empty] | 51N | I0> | E/F | 0.1-0.05-0.4 | 0.0-0.01-1 | 10A | 0.05
|  |  | ABB | REF615 | 51 | I> | P/F | 0.05-0.01-5.00 | 0.025-0.005-15.000 |  |  |  | 0.8 | 1.1 | EI
[5 empty] | 50 | I>> | P/F Hs | 0.010-0.005-5.000 | 0.025-0.005-15.000 |  |  |  | 14.6 | 0.05 | DT
[5 empty] | 51N | I0> | EF | 0.1-0.01-40.00 | 40-10-200000 (ms) |  |  |  | 0.2 | 1.1 | EI
[5 empty] | 50N | I0>> | E/F Hs | 0.1-0.01-40.00 | 40-10-200000 (ms) |  |  |  | 0.5 | 0.05 | DT
11 | I/C ETP TR | 100/1 | Jyoti | JTRSA | 51 | I> | P/F | 0.5-0.25-2 | 0.0-0.01-1 | 100A | [6 empty] | CT2_I/C_ETP TR
[5 empty] | 51N | I0> | E/F | 0.1-0.05-0.4 | 0.0-0.01-1
11 | O/G CRDL TR | 100/5 | Alstom | CDG31 | 51 | I> | P/F | 0.5-0.25-2 | 0.0-0.01-1 | 100A | 0.3 | [5 empty] | CT_I/C_CRDL TR
[5 empty] | 51N | I0> | E/F | 0.1-0.05-0.4 | 0.0-0.01-1 | 20A | 0.05
|  |  | ABB | REF615 | 51 | I> | P/F | 0.05-0.01-5.00 | 0.025-0.005-15.000 |  |  |  | 1.26 | 0.2 | NI
[5 empty] | 50 | I>> | P/F Hs | 0.010-0.005-5.000 | 0.025-0.005-15.000 |  |  |  | 21.2 | 0.05 | DT
[5 empty] | 51N | I0> | EF | 0.1-0.01-40.00 | 40-10-200000 (ms) |  |  |  | 0.2 | 0.2 | NI
[5 empty] | 50N | I0>> | E/F Hs | 0.1-0.01-40.00 | 40-10-200000 (ms) |  |  |  | 0.5 | 0.05 | DT
12 | O/G ZN MELT TR | 100/5 | Alstom | CDG31 | 51 | I> | P/F | 0.5-0.25-2 | 0.0-0.01-1 | 75A | 0.1 | [5 empty] | CT_I/C _ZN MELT TR
[5 empty] | 51N | I0> | E/F | 0.1-0.05-0.4 | 0.0-0.01-1 | 20A | 0.1
|  |  | ABB | REF615 | 51 | I> | P/F | 0.05-0.01-5.00 | 0.025-0.005-15.000 |  |  |  | 1.13 | 6.3 | EI
[5 empty] | 50 | I>> | P/F Hs | 0.010-0.005-5.000 | 0.025-0.005-15.000 |  |  |  | 14.6 | 0.05 | DT
[5 empty] | 51N | I0> | EF | 0.1-0.01-40.00 | 40-10-200000 (ms) |  |  |  | 0.2 | 0.2 | EI
[5 empty] | 50N | I0>> | E/F Hs | 0.1-0.01-40.00 | 40-10-200000 (ms) |  |  |  | 0.5 | 0.05 | DT
13 | O/G COLONY | 50/5 | Alstom | P154 | 51 | I> | P/F | 0.05-0.01-4 | 0.025-0.005-1.2 | 50A | 1.1 | EI | 1 | 1 | NI |  | CT_I/C_COLONY
[5 empty] | 50 | I>> | P/F Hs | 0.05-0.01-35.00 | 0-0.01-100 (s) |  |  |  | 35 | 0.2 | DT
[5 empty] | 51N | I0> | EF | 0.05-0.01-4 | 0.025-0.005-1.2 | 30 | 0.9 | VI | 0.2 | 1 | NI
[5 empty] | 50N | I0>> | E/F Hs | 0.002-0.001-2.00 | 0-0.01-200 (s) |  |  |  | 0.5 | 0.2 | DT

## 11kV Bus Control Room (hidden)
11kV BUS CONTROL ROOM
Department |  |  | Author |  | Status | [7 empty] | Date |  | Lang.
Power Consulting |  |  | Pritul Panchal |  | Rev A | [7 empty] | 2023-12-28 |  | en
sr. No | FeederType or Location | CT Ratio Amps | Relay Make | Relay Type | Relay NEMA Code | IEC Code | Prot Type | Relay Range |  | Exisitng Setting |  |  | Proposed Setting |  |  | Remark
[8 empty] | Plug setting range | Time setting range (s) / TMs range | Plug setting | Time setting (s) / TMs | Charact eristic | Plug setting | Time setting (s) / TMs | Charact eristic
11kV Control Room
1 | I/C CONTROL ROOM BUS | 125/5 | Jyoti | JTRSA | 51 | I> | P/F | 0.5-0.25-2 | 0.0-0.01-1 | 100A | 0.4 |  | 1 | 0.15 | NI |  | CT2_O/G_CONTROL ROOM BUS
[5 empty] | 51N | I0> | E/F | 0.1-0.05-0.4 | 0.0-0.01-1 | 75A | 0.4 |  | 0.2 | 0.15 | NI
2 | O/G SS-5 RTP TR | 125/5 | Jyoti | JTRSA | 51 | I> | P/F | 0.5-0.25-2 | 0.0-0.01-1 | 125A | 0.5 |  | 1 | 0.2 | NI |  | CT_I/C_SS-5_RTP TR
[5 empty] | 50 | I>> | P/F Hs | 4-6-8-10-12-16-20 | 0.02 | 125A | 0.02 |  | 19 | 0.01 | DT
[5 empty] | 51N | I0> | E/F | 0.1-0.05-0.4 | 0.0-0.01-1 | 125A | 0.05 |  | 0.2 | 0.2 | NI
3 | O/G AUX TR-2 (CTRL RM) | 125/5 | Jyoti | JTRSA | 51 | I> | P/F | 0.5-0.25-2 | 0.0-0.01-1 | 93.75A | 10 |  | 1 | 0.5 | NI |  | CT_I/C_AUX TR-2 (CTRL RM)
[5 empty] | 50 | I>> | P/F Hs | 4-6-8-10-12-16-20 | 0.02 | 93.75A |  |  | 20 | 0.01 | DT
[5 empty] | 51N | I0> | E/F | 0.1-0.05-0.4 | 0.0-0.01-1 | 75A | 1 |  | 0.2 | 0.15 | NI
4 | O/G PHE TR | 125/5 | Jyoti | JTRSA | 51 | I> | P/F | 0.5-0.25-2 | 0.0-0.01-1 | 100A | 0.4 |  | 1 | 0.2 | NI |  | CT_I/C_PHE TR
[5 empty] | 50 | I>> | P/F Hs | 4-6-8-10-12-16-20 | 0.02 | 100A |  |  | 19.4 | 0.01 | DT
[5 empty] | 51N | I0> | E/F | 0.1-0.05-0.4 | 0.0-0.01-1 | 93.75A | 0.4 |  | 0.2 | 0.2 | NI

## 6.6kV Bus (hidden)
6.6kV Bus 2EPU-423
Department |  |  | Author |  | Status | [7 empty] | Date |  | Lang.
Power Consulting |  |  | Pritul Panchal |  | Rev A | [7 empty] | 2023-12-28 |  | en
sr. No | FeederType or Location | CT Ratio Amps | Relay Make | Relay Type | Relay NEMA Code | IEC Code | Prot Type | Relay Range |  | Exisitng Setting |  |  | Proposed Setting |  |  | Remark
[8 empty] | Plug setting range | Time setting range (s) / TMs range | Plug setting | Time setting (s) / TMs | Charact eristic | Plug setting | Time setting (s) / TMs | Charact eristic
6.6kV Bus 2EPU-423
1 | O/G AUX TR-1 | 3200A rating | L&T | DN1 Release | L |  | O/L | 0.75 .. 1.0 |  | 1 |  |  | 1 |  |  |  | CB_O/G_AUX TR-1
[5 empty] | S |  | S/C | 7kA & 8.9kA | 0.025
|  | 100/5 | English Electric | CAG14 | 51N | I0> | EF | 10%-40% 20%-80% | 0.025 |  | 0.025 | EI | 0.8 | 0.025 | DT |  | CT_O/G_AUX TR-1
2 | O/G AUX TR-2 |  | Not Available | [13 empty] | CT_O/G_AUX TR-2
3 | O/G TR |  | Not Available
1 | O/G SO2 GAS BLOWER (R-11) |  | Not Available | [13 empty] | CT_O/G_M_SO2 GAS BLOWER (R-11)
1 | O/G ROASTER-II (AIR BLOWER) |  | Not Available | [13 empty] | CT_O/G_ROASTER-II (AIR BLOWER)

## 11kV MRSS (hidden)
11kV MRSS
Department |  |  | Author |  | Status | [7 empty] | Date |  | Lang.
Power Consulting |  |  | Pritul Panchal |  | Rev A | [7 empty] | 2023-12-28 |  | en
sr. No | FeederType or Location | CT Ratio Amps | Relay Make | Relay Type | Relay NEMA Code | IEC Code | Prot Type | Relay Range |  | Exisitng Setting |  |  | Proposed Setting |  |  | Remark
[8 empty] | Plug setting range | Time setting range (s) / TMs range | Plug setting | Time setting (s) / TMs | Charact eristic | Plug setting | Time setting (s) / TMs | Charact eristic
11kV MRSS Bus - A
1 | I/C DG SUPPLY (From DG Sec A Bus B) | 1600/5 | Jyoti | JTRSA | 51 | I> | P/F | 0.5-0.25-2 | 0.0-0.01-1 | 240A | 0.4 |  | 0.5 | 0.15 | NI |  | CT _ O/G_R2 DG SUPPLY 2
[5 empty] | 51N | I0> | E/F | 0.1-0.05-0.4 | 0.0-0.01-1 | 64A | 0.45 |  | 0.2 | 0.15 | NI
2 | O/G CONTROL ROOM BUS | 400/5 | Jyoti | JTRSA | 51 | I> | P/F | 0.5-0.25-2 | 0.0-0.01-1 | 800A | 1 |  | 1 | 0.15 | NI |  | CT_O/G_CONTROL ROOM BUS
[5 empty] | 51N | I0> | E/F | 0.1-0.05-0.4 | 0.0-0.01-1 | 160A | 0.4 |  | 0.2 | 0.15 | NI
3 | O/G AUX TR-1 | 50/5 | Jyoti | JTRSA | 51 | I> | P/F | 0.5-0.25-2 | 0.0-0.01-1 | 37.5A | 0.5 |  | 1.25 | 0.15 | NI |  | CT_I/C_AUX TR-1
[5 empty] | 50 | I>> | P/F Hs | 4-6-8-10-12-16-20 | 0.02 |  |  |  | 20 | 0.02 | DT
|  |  | Alstom | CAG14 | 51N | I0> | E/F | 0.1-0.05-0.4 | 0.025 | 10A |  |  | 0.8 | 0.025 | DT
4 | O/G AUX TR-2 | 50/5 | Jyoti | JTRSA | 51 | I> | P/F | 0.5-0.25-2 | 0.0-0.01-1 | 30A | 0.3 |  | 1.25 | 0.15 | NI |  | CT_I/C_AUX TR-2
[5 empty] | 50 | I>> | P/F Hs | 4-6-8-10-12-16-20 | 0.02 |  |  |  | 20 | 0.02 | DT
|  |  | Alstom | CAG14 | 51N | I0> | E/F | 0.1-0.05-0.4 | 0.025 | 10A |  |  | 0.8 | 0.025 | DT
5 | O/G AUX TR-4 | 300/5 | Jyoti | JTRSA | 51 | I> | P/F | 0.5-0.25-2 | 0.0-0.01-1 | 100A | 0.3 | [5 empty] | CT_I/C_AUX TR-4
|  |  | Alstom | CAG14 | 51N | I0> | E/F | 0.1-0.05-0.4 | 0.025 | 20A
|  |  | ABB | REF615 | 51 | I> | P/F | 0.05-0.01-5.00 | 0.025-0.005-15.000 |  |  |  | 1.13 | 0.94 | EI
[5 empty] | 50 | I>> | P/F Hs | 0.010-0.005-5.000 | 0.025-0.005-15.000 |  |  |  | 20.6 | 0.05 | DT
[5 empty] | 51N | I0> | EF | 0.1-0.01-40.00 | 40-10-200000 (ms)
[5 empty] | 50N | I0>> | E/F Hs | 0.1-0.01-40.00 | 40-10-200000 (ms) |  |  |  | 0.5 | 0.05 | DT
6 | O/G AUX TR-5 | 100/5 | Jyoti | JTRSA | 51 | I> | P/F | 0.5-0.25-2 | 0.0-0.01-1 | 200A | 0.4
|  |  | Alstom | CAG14 | 51N | I0> | E/F | 0.1-0.05-0.4 | 0.025 | 20A
11kV MRSS Bus - B
6 | I/C TR-1A (BHEL Tr) | 1600/5 | Jyoti | JTRSA | 51 | I> | P/F | 0.5-0.25-2 | 0.0-0.01-1 | 1920A | 0.5 | [5 empty] | CT_O/G_TR-1A
[5 empty] | 51N | I0> | E/F | 0.1-0.05-0.4 | 0.025 | 320A | 0.5
|  |  | Alstom | CAG14 | 50N | I0>> | E/F Hs | 0.1-0.05-0.4 | 0.025 | 480A
|  |  | ABB | REF615 | 51 | I> | P/F | 0.05-0.01-5.00 | 0.025-0.005-15.000 |  |  |  | 1 | 0.47 | NI
[5 empty] | 50 | I>> | P/F Hs | 0.010-0.005-5.000 | 0.025-0.005-15.000 |  |  |  | 5 | 0.85 | DT
[5 empty] | 51N | I0> | EF | 0.1-0.01-40.00 | 40-10-200000 (ms)
[5 empty] | 50N | I0>> | E/F Hs | 0.1-0.01-40.00 | 40-10-200000 (ms) |  |  |  | 1 | 0.8 | DT | CBCT of 50/1 is proposed.
7 | I/C SOLAR PP | 800/5 | ABB | REF615 | 51 | I> | P/F | 0.05-0.01-5.00 | 0.025-0.005-15.000 |  |  |  | 1 | 0.36 | NI
[5 empty] | 50 | I>> | P/F Hs | 0.010-0.005-5.000 | 0.025-0.005-15.000 |  |  |  | 3.44 | 0.65 | DT
[5 empty] | 51N | I0> | EF | 0.1-0.01-40.00 | 40-10-200000 (ms)
[5 empty] | 50N | I0>> | E/F Hs | 0.1-0.01-40.00 | 40-10-200000 (ms) |  |  |  | 0.1 | 0.65 | DT
8 | O/G AUX TR-7 | 100/5 | Jyoti | JTRSA | 51 | I> | P/F | 0.5-0.25-2 | 0.0-0.01-1 | 120A | 0.2 | [5 empty] | CT_I/C_AUX TR-7
|  |  | Alstom | CAG14 | 51N | I0> | E/F | 0.1-0.05-0.4 | 0.025 | 20A
|  |  | ABB | REF615 | 51 | I> | P/F | 0.05-0.01-5.00 | 0.025-0.005-15.000 |  |  |  | 1.1 | 1.25 | EI
[5 empty] | 50 | I>> | P/F Hs | 0.010-0.005-5.000 | 0.025-0.005-15.000 |  |  |  | 18.2 | 0.05 | DT
[5 empty] | 51N | I0> | EF | 0.1-0.01-40.00 | 40-10-200000 (ms)
[5 empty] | 50N | I0>> | E/F Hs | 0.1-0.01-40.00 | 40-10-200000 (ms) |  |  |  | 0.5 | 0.05 | DT
9 | O/G ANDREW YULE (VCB PNL BRD) BUS - A | 800/5 | Jyoti | JTRSA | 51 | I> | P/F | 0.5-0.25-2 | 0.0-0.01-1 | 600A | 0.2 | Inverse |  |  |  |  | CT1_O/G_1_ANDREW YULE (VCB PNL BRD)
[5 empty] | 51N | I0> | E/F | 0.1-0.05-0.4 | 0.025 | 160A | 0.1
|  |  | ABB | REF615 | 51 | I> | P/F | 0.05-0.01-5.00 | 0.025-0.005-15.000 |  |  |  | 0.63 | 0.9 | EI
[5 empty] | 50 | I>> | P/F Hs | 0.010-0.005-5.000 | 0.025-0.005-15.000 |  |  |  | 5 | 0.4 | DT
[5 empty] | 51N | I0> | EF | 0.1-0.01-40.00 | 40-10-200000 (ms)
[5 empty] | 50N | I0>> | E/F Hs | 0.1-0.01-40.00 | 40-10-200000 (ms) |  |  |  | 0.12 | 0.4 | DT
10 | O/G AUX TR-6 | 100/5 | Jyoti | JTRSA | 51 | I> | P/F | 0.5-0.25-2 | 0.0-0.01-1 | 100A | 0.2 | [5 empty] | CT_I/C_AUX TR-6
|  |  | Alstom | CAG14 | 50N | I0>> | E/F Hs | 0.1-0.05-0.4 | 0.025 | 20A
|  |  | ABB | REF615 | 51 | I> | P/F | 0.05-0.01-5.00 | 0.025-0.005-15.000 |  |  |  | 1.14 | 1 | EI
[5 empty] | 50 | I>> | P/F Hs | 0.010-0.005-5.000 | 0.025-0.005-15.000 |  |  |  | 19.7 | 0.05 | DT
[5 empty] | 51N | I0> | EF | 0.1-0.01-40.00 | 40-10-200000 (ms)
[5 empty] | 50N | I0>> | E/F Hs | 0.1-0.01-40.00 | 40-10-200000 (ms) |  |  |  | 0.5 | 0.05 | DT
11kV MRSS Bus - C
11 | I/C TR-2A | 1600/5 | Jyoti | JTRSA | 51 | I> | P/F | 0.5-0.25-2 | 0.0-0.01-1 | 1920A | 0.4 | [5 empty] | CT_O/G_TR-2A
[5 empty] | 51N | I0> | E/F | 0.1-0.05-0.4 | 0.025 | 320A | 0.4
|  |  | Alstom | CAG14 | 50N | I0>> | E/F Hs | 0.1-0.05-0.4 | 0.025 | 480A
|  |  | ABB | REF615 | 51 | I> | P/F | 0.05-0.01-5.00 | 0.025-0.005-15.000 |  |  |  | 1 | 0.48 | EI
[5 empty] | 50 | I>> | P/F Hs | 0.010-0.005-5.000 | 0.025-0.005-15.000 |  |  |  | 3.13 | 0.6 | DT
[5 empty] | 51N | I0> | EF | 0.1-0.01-40.00 | 40-10-200000 (ms) |  |  |  | 0.2 | 3.005 | EI
[5 empty] | 50N | I0>> | E/F Hs | 0.1-0.01-40.00 | 40-10-200000 (ms) |  |  |  | 0.5 | 0.6 | DT
13 | I/C CP-10 TR (11kV) | 2500/5 | Not Available | [13 empty] | CT_O/G_CP-10 TR_S
12 | O/G ANDREW YULE (VCB PNL BRD) BUS - B | 800/5 | Jyoti | JTRSA | 51 | I> | P/F | 0.5-0.25-2 | 0.0-0.01-1 | 400A | 0.1 | [5 empty] | CT1_O/G_2_ANDREW YULE (VCB PNL BRD)
[5 empty] | 50N | I0>> | E/F Hs | 0.1-0.05-0.4 | 0.025 | 240A
|  |  | ABB | REF615 | 51 | I> | P/F | 0.05-0.01-5.00 | 0.025-0.005-15.000 |  |  |  | 0.63 | 1.7 | EI
[5 empty] | 50 | I>> | P/F Hs | 0.010-0.005-5.000 | 0.025-0.005-15.000 |  |  |  | 5 | 0.4 | DT
[5 empty] | 51N | I0> | EF | 0.1-0.01-40.00 | 40-10-200000 (ms) |  |  |  | 0.2 | 1.7 | EI
[5 empty] | 50N | I0>> | E/F Hs | 0.1-0.01-40.00 | 40-10-200000 (ms) |  |  |  | 0.5 | 0.4 | DT
13 | O/G RECT TR-1 | 800/5 | Jyoti | JTRSA | 51 | I> | P/F | 0.5-0.25-2 | 0.0-0.01-1 | 600A | 0.1 |  | 1.25 | 0.1 | NI |  | CT_O/G_2_RECT TR-1
[5 empty] | 50 | I>> | P/F Hs | 4-6-8-10-12-16-20 | 0.02 |  |  |  | 9.8 | 0.02 | DT
[5 empty] | 51N | I0> | E/F | 0.1-0.05-0.4 | 0.025 | 160A | 0.1 |  | 0.2 | 0.1 | NI

## Solar
11kV Solar Plant
Department |  |  | Author |  | Status | [7 empty] | Date |  | Lang.
Power Consulting |  |  | Pritul Panchal |  | Rev A | [7 empty] | 2023-12-28 |  | en
sr. No | FeederType or Location | CT Ratio Amps | Relay Make | Relay Type | Relay NEMA Code | IEC Code | Prot Type | Relay Range |  | Exisitng Setting |  |  | Proposed Setting |  |  | Proposed Settings updated 19.03.2024 |  |  | Proposed Settings updated 20.03.2024 |  | Remark
[8 empty] | Plug setting range | Time setting range (s) / TMs range | Plug setting | Time setting (s) / TMs | Charact eristic | Plug setting | Time setting (s) / TMs | Charact eristic | Plug setting | Time setting (s) / TMs | Charact eristic
B2
1 | I/C INV ROOM-1 BUS | 250/1 | ABB | REF615 | 51 | I> | P/F | 0.05-0.01-5.00 | 0.025-0.005-15.000 | 1.01 | 0.15 |  | 1 | 0.28 | NI | 0.64 | 0.7 |  | 0.9 | 0.7 |  | OL
[5 empty] | 50 | I>> | P/F Hs | 0.010-0.005-5.000 | 0.025-0.005-15.000 | 2.3 | 0.15 |  | 11 | 0.25 | DT | 2 | 0.07 |  | 2 | 0.07 |  | INSTANTANEOUS OC
[5 empty] | 51N | I0> | EF | 0.1-0.01-40.00 | 40-10-200000 (ms) | 0.1 | 0.15 |  |  |  |  | 0.05 | 0.7 |  | 0.1 | 0.7 |  | EARTH FAULT
[5 empty] | 50N | I0>> | E/F Hs | 0.1-0.01-40.00 | 40-10-200000 (ms) | 0.045 | 0.15 |  | 0.26 | 0.25 | DT | 0.1 | 0.1 |  | 0.1 | 0.1 |  | INSTANTANEOUS EF
2 | O/G INV DUTY TR-1 (INV ROOM-1) | 125/1 | ABB | REJ601 | 51 | I> | P/F | 0.05-0.01-5.00 | 0.025-0.005-15.000 | 1.01 | 0.1 |  | 1.11 | 0.2 | NI | 0.64 | 1 |  | 0.9 | 1 |  | OL
[5 empty] | 50 | I>> | P/F Hs | 0.010-0.005-5.000 | 0.025-0.005-15.000 | 2.3 | 0.1 |  | 22 | 0.05 | DT | 2 | 0.1 |  | 2 | 0.1 |  | INSTANTANEOUS OC
[5 empty] | 51N | I0> | EF | 0.1-0.01-40.00 | 40-10-200000 (ms) | 1.1 | 0.1 |  |  |  |  | 0.05 | 1 |  | 0.1 | 1 |  | EARTH FAULT
[5 empty] | 50N | I0>> | E/F Hs | 0.1-0.01-40.00 | 40-10-200000 (ms) | 0.5 | 0.05 |  | 0.5 | 0.05 | DT | 0.1 | 0.15 |  | 0.1 | 0.15 |  | INSTANTANEOUS EF
3 | O/G INV DUTY TR-1 (INV ROOM-1) | 125/1 | ABB | REJ601 | 51 | I> | P/F | 0.05-0.01-5.00 | 0.025-0.005-15.000 | 1.01 | 0.1 |  | 1.11 | 0.2 | NI | 0.64 | 1 |  | 0.9 | 1 |  | OL
[5 empty] | 50 | I>> | P/F Hs | 0.010-0.005-5.000 | 0.025-0.005-15.000 | 2.3 | 0.1 |  | 22 | 0.05 | DT | 2 | 0.1 |  | 2 | 0.1 |  | INSTANTANEOUS OC
[5 empty] | 51N | I0> | EF | 0.1-0.01-40.00 | 40-10-200000 (ms) | 0.1 | 0.1 |  |  |  |  | 0.05 | 1 |  | 0.1 | 1 |  | EARTH FAULT
[5 empty] | 50N | I0>> | E/F Hs | 0.1-0.01-40.00 | 40-10-200000 (ms) | 0.5 | 0.15 |  | 0.5 | 0.05 | DT | 0.1 | 0.15 |  | 0.1 | 0.15 |  | INSTANTANEOUS EF
MCR
4 | I/C Main Solar Bus | 750/1 | ABB | REF615 | 51 | I> | P/F | 0.05-0.01-5.00 | 0.025-0.005-15.000 | 1.01 | 0.02 |  | 1 | 0.28 | NI | 0.95 | 0.28 |  | 0.95 | 0.28 |  | OL
[5 empty] | 50 | I>> | P/F Hs | 0.010-0.005-5.000 | 0.025-0.005-15.000 | 2.3 | 0.31 |  | 3.44 | 0.45 | DT | 2 | 0.1 |  | 2 | 0.1 |  | INSTANTANEOUS OC
[5 empty] | 51N | I0> | EF | 0.1-0.01-40.00 | 40-10-200000 (ms) | 0.1 | 0.31 |  |  |  |  | 0.1 | 0.31 |  | 0.1 | 0.31 |  | EARTH FAULT
[5 empty] | 50N | I0>> | E/F Hs | 0.1-0.01-40.00 | 40-10-200000 (ms) | 0.045 | 0.25 |  | 0.1 | 0.45 | DT | 0.1 | 0.15 |  | 0.1 | 0.15 |  | INSTANTANEOUS EF
5 | O/G INV ROOM-1 BUS | 250/1 | ABB | REJ601 | 51 | I> | P/F | 0.05-0.01-5.00 | 0.025-0.005-15.000 | 1.01 | 0.2 |  | 1 | 0.28 | NI | 0.64 | 1 |  | 0.9 | 0.7 |  | OL
[5 empty] | 50 | I>> | P/F Hs | 0.010-0.005-5.000 | 0.025-0.005-15.000 | 2.3 | 0.25 |  | 11 | 0.25 | DT | 2 | 0.1 |  | 2 | 0.07 |  | INSTANTANEOUS OC
[5 empty] | 51N | I0> | EF | 0.1-0.01-40.00 | 40-10-200000 (ms) | 0.1 | 0.2 |  |  |  |  | 0.05 | 1 |  | 0.1 | 0.7 |  | EARTH FAULT
[5 empty] | 50N | I0>> | E/F Hs | 0.1-0.01-40.00 | 40-10-200000 (ms) | 0.5 | 0.25 |  | 0.26 | 0.05 | DT | 0.1 | 0.15 |  | 0.1 | 0.1 |  | INSTANTANEOUS EF
6 | O/G INV DUTY TR-1 (CTRL ROOM) | 125/1 | ABB | REJ601 | 51 | I> | P/F | 0.05-0.01-5.00 | 0.025-0.005-15.000 | 1.01 | 0.1 |  | 1.11 | 0.2 | NI | 0.64 | 1 |  | 0.9 | 1 |  | OL
[5 empty] | 50 | I>> | P/F Hs | 0.010-0.005-5.000 | 0.025-0.005-15.000 | 2.3 | 0.1 |  | 22 | 0.05 | DT | 2 | 0.1 |  | 2 | 0.1 |  | INSTANTANEOUS OC
[5 empty] | 51N | I0> | EF | 0.1-0.01-40.00 | 40-10-200000 (ms) | 0.1 | 0.1 |  |  |  |  | 0.05 | 1 |  | 0.1 | 1 |  | EARTH FAULT
[5 empty] | 50N | I0>> | E/F Hs | 0.1-0.01-40.00 | 40-10-200000 (ms) | 0.5 | 0.05 |  | 0.5 | 0.05 | DT | 0.1 | 0.15 |  | 0.1 | 0.15 |  | INSTANTANEOUS EF
7 | O/G INV DUTY TR-2 (CTRL ROOM) | 125/1 | ABB | REJ601 | 51 | I> | P/F | 0.05-0.01-5.00 | 0.025-0.005-15.000 | 1.01 | 0.1 |  | 1.11 | 0.2 | NI | 0.64 | 1 |  | 0.9 | 1 |  | OL
[5 empty] | 50 | I>> | P/F Hs | 0.010-0.005-5.000 | 0.025-0.005-15.000 | 2.3 | 0.1 |  | 22 | 0.05 | DT | 2 | 0.1 |  | 2 | 0.1 |  | INSTANTANEOUS OC
[5 empty] | 51N | I0> | EF | 0.1-0.01-40.00 | 40-10-200000 (ms) | 0.1 | 0.1 |  |  |  |  | 0.05 | 1 |  | 0.1 | 1 |  | EARTH FAULT
[5 empty] | 50N | I0>> | E/F Hs | 0.1-0.01-40.00 | 40-10-200000 (ms) | 0.5 | 0.05 |  | 0.5 | 0.05 | DT | 0.1 | 0.15 |  | 0.1 | 0.15 |  | INSTANTANEOUS EF
8 | O/G Solar Bus | 250/1 | ABB | REJ601 | 51 | I> | P/F | 0.05-0.01-5.00 | 0.025-0.005-15.000 | 1.01 | 0.2 |  | 1 | 0.28 | NI | 0.64 | 1 |  | 0.9 | 0.7 |  | OL
[5 empty] | 50 | I>> | P/F Hs | 0.010-0.005-5.000 | 0.025-0.005-15.000 | 2.3 | 0.25 |  | 3.44 | 0.45 | DT | 2 | 0.1 |  | 2 | 0.07 |  | INSTANTANEOUS OC
[5 empty] | 51N | I0> | EF | 0.1-0.01-40.00 | 40-10-200000 (ms) | 0.1 | 0.2 |  |  |  |  | 0.05 | 1 |  | 0.1 | 0.7 |  | EARTH FAULT
[5 empty] | 50N | I0>> | E/F Hs | 0.1-0.01-40.00 | 40-10-200000 (ms) | 0.5 | 0.25 |  | 0.1 | 0.45 | DT | 0.1 | 0.15 |  | 0.1 | 0.1 |  | INSTANTANEOUS EF
B3
1 | I/C INV ROOM-1 BUS | 250/1 | ABB | REF615 | 51 | I> | P/F | 0.05-0.01-5.00 | 0.025-0.005-15.000 | 1.01 | 0.15 |  | 1 | 0.28 | NI | 0.64 | 0.7 |  | 0.9 | 0.7 |  | OL
[5 empty] | 50 | I>> | P/F Hs | 0.010-0.005-5.000 | 0.025-0.005-15.000 | 2.3 | 0.15 |  | 11 | 0.25 | DT | 2 | 0.07 |  | 2 | 0.07 |  | INSTANTANEOUS OC
[5 empty] | 51N | I0> | EF | 0.1-0.01-40.00 | 40-10-200000 (ms) | 0.1 | 0.15 |  |  |  |  | 0.05 | 0.7 |  | 0.1 | 0.7 |  | EARTH FAULT
[5 empty] | 50N | I0>> | E/F Hs | 0.1-0.01-40.00 | 40-10-200000 (ms) | 0.045 | 0.15 |  | 0.26 | 0.25 | DT | 0.1 | 0.1 |  | 0.1 | 0.1 |  | INSTANTANEOUS EF
2 | O/G INV DUTY TR-1 (INV ROOM-1) | 125/1 | ABB | REJ601 | 51 | I> | P/F | 0.05-0.01-5.00 | 0.025-0.005-15.000 | 1.01 | 0.1 |  | 1.11 | 0.2 | NI | 0.64 | 1 |  | 0.9 | 1 |  | OL
[5 empty] | 50 | I>> | P/F Hs | 0.010-0.005-5.000 | 0.025-0.005-15.000 | 2.3 | 0.1 |  | 22 | 0.05 | DT | 2 | 0.1 |  | 2 | 0.1 |  | INSTANTANEOUS OC
[5 empty] | 51N | I0> | EF | 0.1-0.01-40.00 | 40-10-200000 (ms) | 0.1 | 0.1 |  |  |  |  | 0.05 | 1 |  | 0.1 | 1 |  | EARTH FAULT
[5 empty] | 50N | I0>> | E/F Hs | 0.1-0.01-40.00 | 40-10-200000 (ms) | 0.5 | 0.05 |  | 0.5 | 0.05 | DT | 0.1 | 0.15 |  | 0.1 | 0.15 |  | INSTANTANEOUS EF
3 | O/G INV DUTY TR-1 (INV ROOM-1) | 125/1 | ABB | REJ601 | 51 | I> | P/F | 0.05-0.01-5.00 | 0.025-0.005-15.000 | 1.01 | 1.2 |  | 1.11 | 0.2 | NI | 0.64 | 1 |  | 0.9 | 1 |  | OL
[5 empty] | 50 | I>> | P/F Hs | 0.010-0.005-5.000 | 0.025-0.005-15.000 | 2.3 | 0.1 |  | 22 | 0.05 | DT | 2 | 0.1 |  | 2 | 0.1 |  | INSTANTANEOUS OC
[5 empty] | 51N | I0> | EF | 0.1-0.01-40.00 | 40-10-200000 (ms) | 0.14 | 1.2 |  |  |  |  | 0.05 | 1 |  | 0.1 | 1 |  | EARTH FAULT
[5 empty] | 50N | I0>> | E/F Hs | 0.1-0.01-40.00 | 40-10-200000 (ms) | 1 | 0.1 |  | 0.5 | 0.05 | DT | 0.1 | 0.15 |  | 0.1 | 0.15 |  | INSTANTANEOUS EF

## 11kV ABB Bus (hidden)
11kV ABB Bus
Department |  |  | Author |  | Status | [7 empty] | Date |  | Lang.
Power Consulting |  |  | Pritul Panchal |  | Rev A | [7 empty] | 2023-12-28 |  | en
sr. No | FeederType or Location | CT Ratio Amps | Relay Make | Relay Type | Relay NEMA Code | IEC Code | Prot Type | Relay Range |  | Exisitng Setting |  |  | Proposed Setting |  |  | Remark
[8 empty] | Plug setting range | Time setting range (s) / TMs range | Plug setting | Time setting (s) / TMs | Charact eristic | Plug setting | Time setting (s) / TMs | Charact eristic
11kV ABB Bus
1 | I/C CP-9 TR | 2500/5 | Not Available | [13 empty] | CT_O/G_CP-9 TR
2 | O/G CAP BANK 7TH | 500/5 | Not Available | [13 empty] | CT_O/G_CAP BANK 7TH
1 | O/G ABB Rect TR-2 | 500/5 | ABB | SPAJ140C | 51 | I> | P/F | 0.05-0.01-5.00 | 0.025-0.005-15.000 | 0.8 | 0.1 |  | 0.24 | 0.2 | NI |  | CT_O/G_ABB Rect TR-2
[5 empty] | 50 | I>> | P/F Hs | 0.010-0.005-5.000 | 0.025-0.005-15.000 | 2.17 | 0.07 |  | 2.87 | 0.05 | DT
[5 empty] | 51N | I0> | EF | 0.1-0.01-40.00 | 40-10-200000 (ms) | 0.29 | 4 |  | 0.2 | 0.2 | NI
[5 empty] | 50N | I0>> | E/F Hs | 0.1-0.01-40.00 | 40-10-200000 (ms) | 0.1 | 0.05 |  | 0.5 | 0.05 | DT

## 11kV Siemens Bus (hidden)
11kV Siemens Bus
Department |  |  | Author |  | Status | [7 empty] | Date |  | Lang.
Power Consulting |  |  | Pritul Panchal |  | Rev A | [7 empty] | 2023-12-28 |  | en
sr. No | FeederType or Location | CT Ratio Amps | Relay Make | Relay Type | Relay NEMA Code | IEC Code | Prot Type | Relay Range |  | Exisitng Setting |  |  | Proposed Setting |  |  | Remark
[8 empty] | Plug setting range | Time setting range (s) / TMs range | Plug setting | Time setting (s) / TMs | Charact eristic | Plug setting | Time setting (s) / TMs | Charact eristic
11kV Siemens Bus - A
1 | I/C TR-1 (From Kirloskar Tr) | 1600/1 | Siemens | 7SJ6001 | 51 | I> | P/F | 0.10 .. 4.00 | 0.05 .. 3.2 | 4 | 0.05 | SI | 0.5 | 1.1 | EI |  | CT_O/G_TR-1_S
[5 empty] | 50 | I>> | P/F Hs | 0.10 .. 25 | 0.00 .. 60.00 | 1.1 | 30 |  | 5 | 0.45 | DT
[5 empty] | 50-1 | I>>> | P/F Hs - 1 | 0.3 .. 12.5 |  | 8
[5 empty] | 51N | I0> | EF | 0.05 .. 4.00 | 0.05 .. 3.2 | 0.1 | 0.1 | SI | 0.2 | 0.45 | DT
[5 empty] | 50N | I0>> | E/F Hs | 0.05 .. 25 | 0.00 .. 60.00 | 0.3 | 30
2 | I/C DG SUPPLY (From DG Sec A Bus B) | 1200/1 | Siemens | 7SJ6001 | 51 | I> | P/F | 0.10 .. 4.00 | 0.05 .. 3.2 | 4 | 0.05 | SI | 0.7 | 0.25 | NI |  | CT_O/G_R3 DG SUPPLY 2
[5 empty] | 50 | I>> | P/F Hs | 0.10 .. 25 | 0.00 .. 60.00 | 1.1 | 30 |  | 2.3 | 0.25 | DT
[5 empty] | 50-1 | I>>> | P/F Hs - 1 | 0.3 .. 12.5 |  | 8
[5 empty] | 51N | I0> | EF | 0.05 .. 4.00 | 0.05 .. 3.2 | 0.2 | 0.5 | SI | 0.2 | 0.24 | NI
[5 empty] | 50N | I0>> | E/F Hs | 0.05 .. 25 | 0.00 .. 60.00 | 4 | 30
3 | O/G ROASTER 3 (SEC-A) | 750/1 | Siemens | 7SJ6001 | 51 | I> | P/F | 0.10 .. 4.00 | 0.05 .. 3.2 | 4 | 0.05 | SI | 0.5 | 3.2 | EI |  | CT_ROASTER 3 (SEC-A) 1
[5 empty] | 50 | I>> | P/F Hs | 0.10 .. 25 | 0.00 .. 60.00 | 2.3 | 25 |  | 5 | 0.25 | DT
[5 empty] | 50-1 | I>>> | P/F Hs - 1 | 0.3 .. 12.5
[5 empty] | 51N | I0> | EF | 0.05 .. 4.00 | 0.05 .. 3.2 | 0.3 | 0.1 | SI
[5 empty] | 50N | I0>> | E/F Hs | 0.05 .. 25 | 0.00 .. 60.00 | 0.3 | 25 |  | 0.3 | 0.25 | DT
4 | O/G CAP BANK 4 | 1600/1 | Siemens | 7SJ6001 | 51 | I> | P/F | 0.10 .. 4.00 | 0.05 .. 3.2 | 0.5 | 0.5 | SI | 1.2 | 0.05 | NI |  | CT_O/G_CAP BANK 4
[5 empty] | 50 | I>> | P/F Hs | 0.10 .. 25 | 0.00 .. 60.00 | 1 | 1 |  | 5 | 0.05 | DT
[5 empty] | 50-1 | I>>> | P/F Hs - 1 | 0.3 .. 12.5 |  | 3
[5 empty] | 51N | I0> | EF | 0.05 .. 4.00 | 0.05 .. 3.2 | 0.3 | 0.5 | SI
[5 empty] | 50N | I0>> | E/F Hs | 0.05 .. 25 | 0.00 .. 60.00 | 0.4 | 1 |  | 0.1 | 0.05 | DT
11kV Siemens Bus - B
5 | I/C TR-2 (From Kirloskar Tr) | 1600/1 | Siemens | 7SJ6001 | 51 | I> | P/F | 0.10 .. 4.00 | 0.05 .. 3.2 | 4 | 0.05 | SI | 1 | 0.27 | EI |  | CT_O/G_TR-2
[5 empty] | 50 | I>> | P/F Hs | 0.10 .. 25 | 0.00 .. 60.00 | 1.1 | 30 |  | 6 | 0.45 | DT
[5 empty] | 50-1 | I>>> | P/F Hs - 1 | 0.3 .. 12.5 |  | 8
[5 empty] | 51N | I0> | EF | 0.05 .. 4.00 | 0.05 .. 3.2 | 0.4 | 0.1 | SI
[5 empty] | 50N | I0>> | E/F Hs | 0.05 .. 25 | 0.00 .. 60.00 | 0.3 | 30 |  | 0.3 | 0.45 | DT
6 | O/G CAP FDR-2 | 1200/1 | Siemens | 7SJ6001 | 51 | I> | P/F | 0.5-0.25-2 | 0.0-0.01-1 | 225A | 0.05 |  | 1.25 | 0.05 | NI |  | CT_O/G_CAP FDR-2
[5 empty] | 51N | I0> | E/F | 0.1-0.05-0.4 | 0.0-0.01-1 | 60A | 0.05 |  | 0.2 | 0.05 | NI
7 | O/G ROASTER 3 (SEC-B) | 750/1 | Siemens | 7SJ6001 | 51 | I> | P/F | 0.10 .. 4.00 | 0.05 .. 3.2 | 4 | 0.05 | SI | 0.5 | 2.4 | EI |  | CT_ROASTER 3 (SECTION B) 1
[5 empty] | 50 | I>> | P/F Hs | 0.10 .. 25 | 0.00 .. 60.00 | 2.3 | 25 |  | 5 | 0.25 | DT
[5 empty] | 50-1 | I>>> | P/F Hs - 1 | 0.3 .. 12.5 |  | 12
[5 empty] | 51N | I0> | EF | 0.05 .. 4.00 | 0.05 .. 3.2 | 0.3 | 0.1 | SI
[5 empty] | 50N | I0>> | E/F Hs | 0.05 .. 25 | 0.00 .. 60.00 | 0.3 | 25 |  | 0.4 | 0.25 | DT
8 | O/G RECTIFIER 3 | 1600/1 | Siemens | 7SJ6001 | 51 | I> | P/F | 0.10 .. 4.00 | 0.05 .. 3.2 | 0.6 | 0.5 | SI | 0.8 | 0.1 | NI |  | CT_RECTIFIER 3
[5 empty] | 50 | I>> | P/F Hs | 0.10 .. 25 | 0.00 .. 60.00 | 1 | 1 |  | 7.4 | 0.05 | DT
[5 empty] | 50-1 | I>>> | P/F Hs - 1 | 0.3 .. 12.5 |  | 3
[5 empty] | 51N | I0> | EF | 0.05 .. 4.00 | 0.05 .. 3.2 | 0.3 | 0.5 | SI
[5 empty] | 50N | I0>> | E/F Hs | 0.05 .. 25 | 0.00 .. 60.00 | 0.4 | 1 |  | 0.2 | 0.05 | DT

## 11kV DG (hidden)
11kV DG
Department |  |  | Author |  | Status | [7 empty] | Date |  | Lang.
Power Consulting |  |  | Pritul Panchal |  | Rev A | [7 empty] | 2023-12-28 |  | en
sr. No | FeederType or Location | CT Ratio Amps | Relay Make | Relay Type | Relay NEMA Code | IEC Code | Prot Type | Relay Range |  | Exisitng Setting |  |  | Proposed Setting |  |  | Remark
[8 empty] | Plug setting range | Time setting range (s) / TMs range | Plug setting | Time setting (s) / TMs | Charact eristic | Plug setting | Time setting (s) / TMs | Charact eristic
11kV DG
1 | I/C AUX TR | 150/5 | ABB | SPAJ141C | 51 | I> | P/F | 0.05-0.01-5.00 | 0.025-0.005-15.000 | 0.84 | 0.25 |  | 0.84 | 0.2 | NI |  | CT_O/G_P_AUX TR
[5 empty] | 50 | I>> | P/F Hs | 0.010-0.005-5.000 | 0.025-0.005-15.000 | 4 | 1 |  | 12 | 0.05 | DT
[5 empty] | 51N | I0> | EF | 0.1-0.01-40.00 | 40-10-200000 (ms) | 7% | 2
[5 empty] | 50N | I0>> | E/F Hs | 0.1-0.01-40.00 | 40-10-200000 (ms) | 18% | 1 |  | 0.5 | 0.05 | DT
2 | I/C CP-10 TR | 2500/5 | ABB | SPAJ141C | 51 | I> | P/F | 0.05-0.01-5.00 | 0.025-0.005-15.000 | 0.84 | 0.25 |  | 1.01 | 0.2 | NI |  | CT_O/G_P_CP-10 TR
[5 empty] | 50 | I>> | P/F Hs | 0.010-0.005-5.000 | 0.025-0.005-15.000 | 4 | 1 |  | 8 | 0.05 | DT
[5 empty] | 51N | I0> | EF | 0.1-0.01-40.00 | 40-10-200000 (ms) | 7% | 2 |  | 0.2 | 0.2 | NI
[5 empty] | 50N | I0>> | E/F Hs | 0.1-0.01-40.00 | 40-10-200000 (ms) | 18% | 1 |  | 0.5 | 0.05 | DT
3 | I/C DG SUPPLY (SEC A BUS B) | 600/5 | Not Available | [6 empty] | 0.84 | [6 empty] | CT_O/G_R3 DG SUPPLY
18%
3 | O/G CP-9 TR | 2500/5 | ABB | SPAJ141C | 51 | I> | P/F | 0.05-0.01-5.00 | 0.025-0.005-15.000 | 0.84 | 0.25 |  | 1.01 | 0.1 | NI |  | CT_O/G_P_CP-9 TR
[5 empty] | 50 | I>> | P/F Hs | 0.010-0.005-5.000 | 0.025-0.005-15.000 | 4 | 1 |  | 8.4 | 0.05 | DT
[5 empty] | 51N | I0> | EF | 0.1-0.01-40.00 | 40-10-200000 (ms) | 7% | 2
[5 empty] | 50N | I0>> | E/F Hs | 0.1-0.01-40.00 | 40-10-200000 (ms) | 18% | 1 |  | 0.12 | 0.05 | DT
5 | O/G DG SUPPLY (11kV Bus A) | 600/5 | Not Available | [13 empty] | CT_O/G_R2 DG SUPPLY

## 132KV (hidden)
132kV Incomer
Department |  |  | Author |  | Status | [7 empty] | Date |  | Lang.
Power Consulting |  |  | Pritul Panchal |  | Rev A | [7 empty] | 2023-12-28 |  | en
sr. No | FeederType or Location | CT Ratio Amps | Relay Make | Relay Type | Relay NEMA Code | IEC Code | Prot Type | Relay Range |  | Exisitng Setting |  |  | Proposed Setting |  |  | Remark
[8 empty] | Plug setting range | Time setting range (s) / TMs range | Plug setting | Time setting (s) / TMs | Charact eristic | Plug setting | Time setting (s) / TMs | Charact eristic
132kV Incomer
1 | O/G TR-1 (Kirloskar) | 150/1 | Siemens | Siprotech 7UT61 | 51 | I> | P/F | 0.05-0.01-5.00 | 0.025-0.005-15.000 | 4 | 0.05 | NI | 0.77 | 0.6 | EI | Siprotech 7UT61 Siemens | CT_TR-1
[5 empty] | 50 | I>> | P/F Hs | 0.010-0.005-5.000 | 0.025-0.005-15.000 | 1 | 30 |  | 10.8 | 0.05 | DT
[5 empty] | 51N | I0> | EF | 0.1-0.01-40.00 | 40-10-200000 (ms) | 1 | 0.05 | NI | 0.2 | 1.03 | NI
[5 empty] | 50N | I0>> | E/F Hs | 0.1-0.01-40.00 | 40-10-200000 (ms) | 13 | 0.05 |  | 0.5 | 0.05 | DT
2 | O/G TR-2 (Kirloskar) | 150/1 | Siemens | Siprotech 7UT61 | 51 | I> | P/F | 0.05-0.01-5.00 | 0.025-0.005-15.000 | 4 | 0.05 | NI | 0.77 | 0.49 | NI |  | CT_TR-2
[5 empty] | 50 | I>> | P/F Hs | 0.010-0.005-5.000 | 0.025-0.005-15.000 | 1 | 30 |  | 10.9 | 0.05 | DT
[5 empty] | 51N | I0> | EF | 0.1-0.01-40.00 | 40-10-200000 (ms) | 1 | 0.05 | NI | 0.2 | 0.49 | NI
[5 empty] | 50N | I0>> | E/F Hs | 0.1-0.01-40.00 | 40-10-200000 (ms) | 13 | 0.05 |  | 0.5 | 0.05 | DT
3 | O/G TR-1A (BHEL) | 200/1 | EE | REF615 | 51 | I> | P/F | 0.05-0.01-5.00 | 0.025-0.005-15.000 | 1 | 0.3 | Inverse | 0.79 | 0.5 | NI |  | CT_TR-1A
[5 empty] | 50 | I>> | P/F Hs | 0.010-0.005-5.000 | 0.025-0.005-15.000 |  |  |  | 10.9 | 0.05 | DT
[5 empty] | 51N | I0> | EF | 0.1-0.01-40.00 | 40-10-200000 (ms) | 0.2 | 0.35 | Inverse | 0.2 | 0.5 | NI
[5 empty] | 50N | I0>> | E/F Hs | 0.1-0.01-40.00 | 40-10-200000 (ms) |  |  |  | 0.5 | 0.05 | DT
4 | O/G TR-2A (BHEL) | 200/1 | EE | REF615 | 51 | I> | P/F | 0.05-0.01-5.00 | 0.025-0.005-15.000 | 1 | 0.3 | Inverse | 0.88 | 0.48 | EI |  | CT_TR-2A
[5 empty] | 50 | I>> | P/F Hs | 0.010-0.005-5.000 | 0.025-0.005-15.000 |  |  |  | 10.1 | 0.05 | DT
[5 empty] | 51N | I0> | EF | 0.1-0.01-40.00 | 40-10-200000 (ms) | 0.2 | 0.35 | Inverse | 0.2 | 0.49 | NI
[5 empty] | 50N | I0>> | E/F Hs | 0.1-0.01-40.00 | 40-10-200000 (ms) |  |  |  | 0.5 | 0.05 | DT
5 | 132KV I/C | 350/1 | Siemens | Siprotech 7UT61 | 51 | I> | P/F |  |  | 4 | 0.05 | NI
[5 empty] | 50 | I>> | P/F Hs |  |  | 1.14 | 30
[5 empty] | 51N | I0> | EF |  |  | 1 | 0.05 | NI
[5 empty] | 50N | I0>> | E/F Hs |  |  | Infinity | Infinity
6 | O/G Overhead HZL Bus | 400/5 | ABB | REF615 | 51 | I> | P/F | 0.05-0.01-5.00 | 0.025-0.005-15.000 | [7 empty] | CT_O/H_HZL Bus
[5 empty] | 50 | I>> | P/F Hs | 0.010-0.005-5.000 | 0.025-0.005-15.000
[5 empty] | 51N | I0> | EF | 0.1-0.01-40.00 | 40-10-200000 (ms)
[5 empty] | 50N | I0>> | E/F Hs | 0.1-0.01-40.00 | 40-10-200000 (ms)
7 | I/C Overhead HZL Bus | 350/5 | ABB | REF615 | 51 | I> | P/F | 0.05-0.01-5.00 | 0.025-0.005-15.000 | [7 empty] | CT_O/H_HZL Bus
[5 empty] | 50 | I>> | P/F Hs | 0.010-0.005-5.000 | 0.025-0.005-15.000
[5 empty] | 51N | I0> | EF | 0.1-0.01-40.00 | 40-10-200000 (ms)
[5 empty] | 50N | I0>> | E/F Hs | 0.1-0.01-40.00 | 40-10-200000 (ms)