## Sheet1
[78 empty] | Phase protection | i> 1*In, TMS 0.1S
i>> 2.5*In, DMT 0.1S
i>>> 3*In, 0.1s
[78 empty] | Ground Fault | In1: 0.15*Ien, DMT 0.1s
In2: 0.5*Ien, 0.05s
SOLAR supply
HT Breaker 11kV
SS4
[72 empty] | SS5 |  |  |  | Pyrotech
|  | CTR 250/1 | [18 empty] | I>> 0.7*In, 31s
|  | I> 0.85*In, 30s | [6 empty] | Trafo 11 A |  |  |  | Trafo 11B | [7 empty] | I>>> 7*In, 0.05s
|  | I>> 6.19*In, 0.05s | [18 empty] | Ip 1.5*2n, 2.97s
|  | Ip 4*In, 0.82s | [18 empty] | IEEE>> 0.5*In, 10s
|  | Normal inverse | [18 empty] | Inverse
HT Breaker 3.3kV
|  |  | PCC 111 | [30 empty] | PCC 112 | [15 empty] | PCC 113
[21 empty] | CTR 250/1 | [6 empty] | CTR 300/1 |  | CTR 400/1 |  |  |  |  | CTR 400/1 |  |  |  | CTR 400/1 | CTR 400/1 |  | CTR 600/5 | CTR 300/1 |  |  |  |  | CTR 100/5 | [8 empty] | CTR 400/1 | CTR 400/1 |  |  | CTR 400/1 |  |  | CTR 400/1
spam150c | spam150c | [5 empty] | spam150c | spam150c | spam150c | In: 1000A |  | In: 1000A | spam150c |  |  |  | spam150c | spam150c | spam150c | In: 630A | spam150c | In: 630A | In: 630A |  | In: 1000A | In: 630A | In: 630A | spam150c | spam150c | spam150c | In: 630A |  | spam150c | In: 1000A | spam150c | In: 630A | In: 1000A | In: 1000A | spam150c | spam150c |  | In: 1000A | spam150c |  | In: 1000A | spam150c | spam150c | In: 1000A | In: 630A | In: 630A |  |  | CTR 300/1 | CTR 300/1 | In: 630A |  | spam150c | spam150c | In: 630A | spam150c | spam150c | In: 1000A | In: 1000A | spam150c
|  | In: 4000A | In: 1000A | In: 630A | In: 630A | In: 630A |  |  |  | L: 0.8, 3.5 |  | L: 0.8, 3.5 |  | In: 4000A | In: 1000A | In: 630A |  |  |  | L: 1, 10 |  | L: 0.8, 2 | L: 0.8, 2 |  | L: 0.8, 2 | L: 0.8, 2 | L: 0.8, 2 |  |  |  | L: 0.8, 2 | In: 4000A |  | L: 0.8, 3.5 |  | L: 0.8, 2 | L: 0.8, 3.5 | L: 0.8, 3.5 |  |  | In: 4000A | L: 0.9, 21 |  | In: 630A | L: 0.8, 3.5 |  |  | L: 0.4, 2 | L: 0.8, 2 | L: 1, 2 | In: 4000A | spam150c | spam150c | spam150c | L: 0.8, 2 |  |  |  | L: 0.8, 2 | CTR 400/1 |  | L: 0.8, 3.5 | L: 0.6, 2 |  | CTR 400/1 | In: 4000A
|  | L: 0.9, 21 | L: 0.8, 3.5 | L: 0.8, 2 | L: 0.8, 2 | L: 0.8, 2 |  |  |  | S: 12, 0.4 |  | S: 12, 0.4 |  | L: 1 | L: 0.8, 3.5 | L: 0.8, 2 |  |  |  | S: 3, OFF |  | S: 12, 0.2 | S: 12, 0.2 |  | S: 12, 0.2 | S: 12, 0.2 | S: 12, 0.2 |  |  |  | S: 12, 0.2 | L: 1, 21 |  | S: 12, 0.4 |  | S: 12, 0.2 | S: 12, 0.4 | S: 12, 0.4 |  |  | L: 1, 21 | S: 6, 0.4 |  | L: 0.5 | S: 12, 0.4 |  |  | S: 1.25, 0.1 | S: 12, 0.2 | S: 12, 0.2 | L: 1, 21 |  |  |  | S: 12, 0.2 |  |  |  | S: 12, 0.2 |  |  | S: 12, 0.4 | S: 3, 0.1 |  | In: 1000A | L: 1, 21
|  | S: 10 | S: 12, 0.4 | S: 12, 0.2 | S: 12, 0.2 | S: 12, 0.2 |  |  |  | I: 12 |  | I: 12 |  | S: 6, 0.3 | S: 12, 0.4 | S: 12, 0.2 |  |  |  | I: 3 |  | I: 8 | I: 8 |  | I: 12 | I: 8 | I: 8 |  |  |  | I: 8 | S: 12, 0.4 |  | I: 12 |  | I: 8 | I: 12 | I: 12 |  |  | S: 6, 0.4 | I: 3 |  | S: 3, 0.4 | I: 12 |  |  | I: 12 | I: 8 | I: 8 | S: 6, 0.4 |  |  |  | I: 8 |  |  |  | I: 8 |  |  | I: 12 | I: 4 |  | L: 0.8, 3.5 | S: 6, 0.4
|  | I: 10 | I: 12 | I: 8 | I: 8 | I: 8 |  |  |  | G: D, 0.2 |  | G: D, 0.2 |  | I: 8 | I: 12 | I: 8 |  |  |  | G: E, 0.1 |  | G: D, 0.1 | G: D, 0.1 |  | G: D, 0.2 | G: D, 0.1 | G: D, 0.1 |  |  |  | G: D, 0.1 | I: 8 |  | G: D, 0.2 |  | G: D, 0.1 | G: D, 0.2 | G: D, 0.2 |  |  | I: 8 | G: D,B,0.3 |  | I: Ii >= 20*In | G: D, 0.2 |  |  | G: A,B, 0.1 | G: D, 0.1 | G: D, 0.1 | I: 8 |  |  |  | G: D, 0.1 |  |  |  | G: D, 0.1 |  |  | G: D, 0.2 | G: D, 0.1 |  | S: 12, 0.4 | I: 8
|  | G: 10 | G: D, 0.2 | G: D, 0.1 | G: D, 0.1 | G: D, 0.1 | [7 empty] | G: D, 0.3 | G: D, 0.2 | G: D, 0.1 | [15 empty] | G: D, 0.2 | [8 empty] | G: D, 0.3 |  |  | G: C, 0.5 | [6 empty] | G: D, 0.8 | [13 empty] | I: 12 | G: E, 0.3
G: D, 0.2
MCC116
| MCC 114 | [18 empty] | PDB 111 | [6 empty] | MCC 113
In: 1000A
| In: 1000A |  |  |  |  | L: 0.8, 10s(6*Ir) | [14 empty] | In : 1000A |  |  | In :1000A
| L: 0.8, 10s(6*Ir) |  |  |  |  | S: 3, 0.3 |  |  |  |  | MCC115 | [9 empty] | L: 0.45, 3.5 |  |  | L: 0.4, 2
| S: 3, 0.3 |  |  |  |  | I: Ii >= 20*In | [14 empty] | S: 1.5,0.4 |  |  | S: 1.5, 0.2
| I: Ii >= 20*In |  |  |  |  | G: C, 0.5 |  |  |  |  | In: 800A |  |  |  |  | In: 800A |  |  |  |  | I: 2.2 |  |  | I: 1.5
| G: C, 0.5 | [9 empty] | L: 1, 10s(6*Ir) |  |  |  |  | L: 1, 10s(6*Ir) |  |  |  |  | G:B, 0.2 |  |  | G: B, 0.1
[11 empty] | S: 6, 0 |  |  |  |  | S: 6, 0
| MCC 111 | [9 empty] | I: Ii >= 20*In |  |  |  |  | I: Ii >= 20*In |  |  |  | PDB 112
[11 empty] | G:off, 0 |  |  |  |  | G:off, 0
| In: 800A | [19 empty] | In : 1000A |  |  | In : 1000A
| L: 1, 10s(6*Ir) |  |  |  | In: 800A | [15 empty] | L: 1, 10 |  |  | L: 1, 10
| S: 6, 0 |  |  |  | L: 1, 10s(6*Ir) | [5 empty] | MCC112 | [9 empty] | S: 3, 4 |  |  | S: 3, 4
| I: Ii >= 20*In |  |  |  | S: 6, 0 | [15 empty] | I: 3 |  |  | I: 3
| G:off, 0 |  |  |  | I: Ii >= 20*In | [5 empty] | In: 800A |  |  |  |  | In: 800A |  |  |  |  | G: off, 0.5 |  |  | G: off, 0.5
[5 empty] | G:off, 0 | [5 empty] | L: 1, 10s(6*Ir) |  |  |  |  | L: 1, 10s(6*Ir)
[11 empty] | S: 6, 0 |  |  |  |  | S: 6, 0
[11 empty] | I: Ii >= 20*In |  |  |  |  | I: Ii >= 20*In
[11 empty] | G:off, 0 |  |  |  |  | G:off, 0
SOLAR supply
| Overload | L
| Short Circuit | S
| Instantaneous | I | [78 empty] | 0.95, 0.28
| Ground | G | [74 empty] | HT_1 + HT_2 + B_2 + B_3= 125+125+250+250 |  |  |  | 2, 0.1
[51 empty] | 250A breaker | [16 empty] | 250A breaker | [8 empty] | breaker-125A |  | breaker- 750A VCB |  | 0.1, 0.31 | breaker-125A
[50 empty] | 0.9, 0.7 | [16 empty] | 0.9, 0.7 | [8 empty] | 0.9, 1 |  |  |  |  | 0.1, 0.15 |  | 0.9, 1
[50 empty] | 2, 0.07 | [16 empty] | 2, 0.07 | [8 empty] | 2, 0.1 | [6 empty] | 2, 0.1
[50 empty] | 0.1, 0.7 | [16 empty] | 0.1, 0.7 | [8 empty] | 0.1, 1 | [6 empty] | 0.1, 1
[46 empty] | breaker-125A |  |  |  | 0.1, 0.1 | [5 empty] | breaker-125A | [10 empty] | 0.1, 0.1 | [8 empty] | 0.1, 0.15 |  |  |  |  | change over switch |  | 0.1, 0.15
[63 empty] | breaker-125A | [6 empty] | breaker-125A
[45 empty] | 0.9, 1 | [11 empty] | 0.9, 1 |  |  |  |  | 0.9, 1 | [8 empty] | 0.9, 1
[45 empty] | 2, 0.1 | [11 empty] | 2, 0.1 |  |  |  |  | 2, 0.1 | [8 empty] | 2, 0.1
[45 empty] | 0.1, 1 | [11 empty] | 0.1, 1 |  |  |  |  | 0.1, 1 | [8 empty] | 0.1, 1
[45 empty] | 0.1, 0.15 | [11 empty] | 0.1, 0.15 |  |  |  |  | 0.1, 0.15 | [8 empty] | 0.1, 0.15
(2.2*10^6)/11*10^3*1.732 ~=115A (rated)
~1500A
Breaker 1600A
Breaker- 1600A ACB
~1500A
[43 empty] | Breaker 1600A | [8 empty] | Breaker 1600A | [6 empty] | Breaker 1600A | [9 empty] | Breaker 1600A | [14 empty] | Overcurrent
Overcurrent Instantaneous
Earth Fault
[80 empty] | Breaker 1600A |  |  |  | Earth Fault Instantaneous
Breaker - 1600A
180A*8SMB =1440A
[43 empty] | Breaker 1600A | [8 empty] | Breaker 1600A | [6 empty] | Breaker 1600A | [9 empty] | Breaker 1600A
[74 empty] | breaker- 200A | [5 empty] | breaker200A
15A*12strings = 180A
[43 empty] | breaker200A | [8 empty] | breaker200A | [6 empty] | breaker200A |  |  |  |  | breaker200A |  |  |  |  | breaker200A
132 kV incomer from RSEB
O/G trafo 1 (Kirloskar)(20MVA/25MVA)
O/G trafo 2 (Kirloskar)(20MVA/25MVA)
O/G 40MVA TRAFO -1 (New MCR)
O/G 40MVA TRAFO -2 (New MCR)
O/G 40MVA TRAFO -3 (New MCR)
SF6 breaker
SF6 breaker
SF6 breaker
SF6 breaker
SF6 breaker
SF6 breaker
Siemens Bus
I/C from Trafo 1
BUS PT 1
CAPACITOR BANK 4
DG INCOMER 1
PHE Trafo
O/G to R3 SEC A
BUS Coupler
Siemens Bus
I/C from Trafo 2
Adaptor BUS PT
ABB Rectifier 3
O/G to Zinc Melting Trafo
O/G to R3 SEC B
New MCR Panel
I/C 40MVA TRAFO -1
O/G to Jyoti Panel 12S
3150A VCB
O/G to R6 SEC A
BUS Coupler 1
2500A VCB
New MCR Panel
I/C 40MVA TRAFO -2
2500A VCB
3150A VCB
11kV 3500A BUS 2A
Spare
O/G to Andrew Yule Panel 9
1250A VCB
1250A VCB
11kV 3500A BUS 2B
Spare
O/G to Andrew Yule Panel 7
1250A VCB
1250A VCB
New MCR Panel
I/C 40MVA TRAFO -3
3150A VCB
O/G TO R6 SEC B
O/G to Jyoti Panel 4S
SPARE
2500A VCB
2500A VCB
1250A VCB
BUS-A_CDSS S/S SW-12 I/C
BUS-B_CDSS S/S SW-12 I/C
3150A VCB
BUS Coupler 2
3150A VCB
Bus Coupler 1
Bus PT 1
1800 kVA Trafo 6
O/G to Andrew Yule I/C 2
Spare
I/C from MCR panel 1
12MW supply from solar plant
BUS Coupler 2
1800kVA Trafo 3
1000kVA Trafo 1 (MCTP O/G supply)
4 Panel Board Supply
1800kVA Trafo 4
1000kVA Trafo 2
11/6.6kV 5000kVA Trafo
Diesel Generator Supply
ABB Capacitor Bank
ABB Rectifier 2
CP- 09 from Wartsila
Bus PT 2
I/C from MCR panel 20 (4S)
Capacitor No. 2
O/G to Andrew Yule I/C 2
Rectifier Trafo No. 1
CP- 10 from Wartsila
Spare
1800kVA Trafo 1
Spare
Spare
Spare
Capacitor No. 3
I/C from Jyoti Panel 2
Bus Coupler
STG
Capacitor PFIC II
Spare
SO2 Blower 2.8MW
O/G to Trafo 111A
BUS PT 1
O/G to Trafo 112A
O/G to Trafo 113A
Spare
STG I/C 1, 10MW, IC014
O/G to Trafo 11-A
I/C 1 from MRS FDR No. 5
BUS Coupler
BUS PT 2
I/C 2 from MRS FDR No. 11
O/G to Trafo 11-B
Capacitor PFIC - 12
STG I/C 2, 10MW, IC014
O/G to Trafo 111 B
O/G to Trafo 112 B
O/G to Trafo 113 B
R6 Project Trafo
Spare
RAB 1320 kW
Spare
R0 ZLD
Colony Trafo
Spare
CRDL 2MVA Trafo
ETP Trafo 1250kVA
Dariba Pump House
Capacitor No. 1
Spare
I/C from Jyoti Panel 10
Spare
BUS PT 100VA
Spare
Ball Mill 300kW
I/C -1 from 11kV FDR No. 10
BUS Coupler
BUS PT
I/C 2 from 11kV FDR No. 15
FWP WHRB 200kW
CWP WHRB 220kW
Start Up Fan 250kW
Spare
Spare
Spare
I/C TR 111A from 11kV panel FDR No. 4
MCC 114 I/C 1
Spare
MCC 112 I/C 2
MCC 115 I/C 1
CT
Screw Comp - 1
CT 5 Pump 1
PDB 111 I/C 2
Bus Coupler
Adaptor
MCC 118 I/C 1
I/C 2 TR 111B from 11kV Panel FDR no. 18
PDB 112 I/C
CLDC MCC
DT 110kW
SCREW COMP 2
New CWP CC
Spare
FAT 110kW
MCC 111 I/C 1
MCC 113 RMH
MCC 113 RMH
WGP3
WGP 4
CT 4 Pump 1
Screw Comp 3
CT 2 Pump 1
WGP 1
I/C Trafo 112A from 11kV Panel FDR No. 6
CT 1 Pump 3
MCC 116 I/C 1
MCC 112 I/C 1
CT 2 Pump 2
Screw Comp 4
I/C 2 TR 112B from 11kV Panel FDR No. 19
IAT
CT 4 Pump 3
Acid Pump from Interim Absorption System
Spare
vc
PDB 112 I/C
IR 3 160kW Compressor House
CT 4 Pump 2
GA 55 R3 Comp 6
MCC 115 I/C 2
MCC 114 I/C 2
I/C 1 TR 113A from 11kV panel FDR No. 7
CT 1 PUMP 4
Cooling Air Fan 200kW
PAH for HGP
MCC 118 I/C 2
BUS Coupler
Adaptor
CT 2 PUMP 3
CT 5 PUMP 2
WGP 2
New Cooling Air Fan 45kW
IR Comp No. 5 R III
MCC 111 I/C 2
Spare (PJB GCP)
CT 1 Pump 1
Pump House 1 Filtration MCC I/C 2
I/C 2 TR 113B from 11kV panel FDR no. 20
vc
vc
H- pole 11kV transmission line
HT Panel -1 (11kV) I/C
HT Panel (outgoing)
HT Panel -2 (11kV) I/C
Inverter 1
DC Switch
(800V DC)
IGBT (AC to DC)
Inverter
AC Switch (380V AC)
SMB (800V DC)
PV Area (800V DC)
Inverter 2
DC Switch
(800V DC)
SMB (800V DC)
PV Area (800V DC)
Inverter
AC Switch (380V AC)
IGBT (AC to DC)
Inverter 3 DC Switch
(800V DC)
IGBT (AC to DC)
Inverter
AC Switch (380V AC)
SMB (800V DC)
PV Area (800V DC)
Inverter 3 DC Switch
(800V DC)
IGBT (AC to DC)
Inverter
AC Switch (380V AC)
SMB (800V DC)
PV Area (800V DC)
IDT-1 380V/11kV
(2.2MVA)
IDT-2 380V/11kV
(2.2MVA)
Aux. Trafo 380V/415V (50kVA)
ACDB (415V)
UPSDB 230V AC
Battery Bank 415V
LDB
SCADA Panel (230V AC)
WMS (230V AC)
I/C supply from PCC 111 FDR no. 14F1
BUS Coupler
I/C supply from PCC 113 FDR no. 11F1
I/C supply from PCC 111 FDR no. 11F1
BUS Coupler
I/C supply from PCC 113 FDR no. 3F2
I/C PCC 112
I/C supply from PCC 111 FDR no. 4F2
BUS Coupler
I/C supply from PCC 113 FDR no. 3F1
I/C supply from PCC 111 FDR no. 4F1
BUS Coupler
I/C supply from PCC 112 FDR no. 9F2
I/C PCC 111 6F-2
BUS Coupler
I/C PCC 112 8F-2
I/C PCC 111 10F1
BUS Coupler
I/C PCC 113 1F1
vc
vc
vc
vc
I/C PCC 111
BUS Coupler
I/C PCC 112
1600kVA Trafo no. 7
MR MCC
2000kVA Trafo
1800kVA Trafo 2
I/C from 11kV main bus panel no. 19
Spare
301-A MCC
O/G to SS1
Spare
O/G to ZE Pyrotech MCC
TGT MCC
R2 BYARD MCC
PH1 Siemens & LnT MCC
L&P 201-B1 MCC
L&P 202-B2 MCC
R2 L&T MCC
BUS Coupler
vc
Cad. 701 MCC
Filter Water MCC PH1
Purification 201 A
ZE 301A MCC
PH2 MCC
M&C GE MCC
Tie Feeder SS5
L&P MCC2
200kVA Trafo 5
Main I/C
Bus Coupler 1
Bus coupler 2
Water Classifier MCC
Spare
Neutral Leaching I/C 2
GE Zinc Melting
Supply to interlac MCC
Spare
Capacitor Control Panel
Spare
Spare
Tie SS6
Spare
O/G to new Melting
Filtration MCC- 03
Capacitor
Neutral Leaching I/C 1
Sulzer
LT Room Admin Block
Induction Furnace PCC Supply
Block 3 I/C
Block 2 I/C
HT Panel -1 (11kV) I/C
HT Panel (outgoing)
HT Panel -2 (11kV) I/C
Inverter 1
DC Switch
(800V DC)
IGBT (AC to DC)
Inverter
AC Switch (380V AC)
SMB (800V DC)
PV Area (800V DC)
Inverter 2
DC Switch
(800V DC)
SMB (800V DC)
PV Area (800V DC)
Inverter
AC Switch (380V AC)
IGBT (AC to DC)
Inverter 3 DC Switch
(800V DC)
IGBT (AC to DC)
Inverter
AC Switch (380V AC)
SMB (800V DC)
PV Area (800V DC)
Inverter 3 DC Switch
(800V DC)
IGBT (AC to DC)
Inverter
AC Switch (380V AC)
SMB (800V DC)
PV Area (800V DC)
IDT-1 380V/11kV
(2.2MVA)
IDT-2 380V/11kV
(2.2MVA)
Aux. Trafo 380V/415V (50kVA)
ACDB (415V)
UPSDB 230V AC
Battery Bank 415V
LDB
SCADA Panel (230V AC)
WMS (230V AC)
HT Panel -1 (11kV) I/C
HT Panel (outgoing)
HT Panel -2 (11kV) I/C
Inverter 1
DC Switch
(800V DC)
IGBT (AC to DC)
Inverter
AC Switch (380V AC)
SMB (800V DC)
PV Area (800V DC)
Inverter 2
DC Switch
(800V DC)
SMB (800V DC)
PV Area (800V DC)
Inverter
AC Switch (380V AC)
IGBT (AC to DC)
Inverter 3 DC Switch
(800V DC)
IGBT (AC to DC)
Inverter
AC Switch (380V AC)
SMB (800V DC)
PV Area (800V DC)
Inverter 3 DC Switch
(800V DC)
IGBT (AC to DC)
Inverter
AC Switch (380V AC)
SMB (800V DC)
PV Area (800V DC)
IDT-1 380V/11kV
(2.2MVA)
IDT-2 380V/11kV
(2.2MVA)
Aux. Trafo 380V/415V (50kVA)
ACDB (415V)
UPSDB 230V AC
Battery Bank 415V
LDB
SCADA Panel (230V AC)
WMS (230V AC)
I/C from SS5 LHS
Capacitor LHS
Capacitor LHS
Capacitor RHS
I/C from SS5 RHS
Capacitor RHS
MCC 116 I/C 2
PDB 111 I/C 1
CT 1 Pump 2
Bus Coupler
Adaptor

## Sheet2
CDSS: Instead of the SO2 blower tripping, the main transformer tripped (it was an earth fault trip). There is no earth fault setting in SO2 Blower. We can instead change the other settings so that the SO2 Blower trips first.
see the rating of the equipment. Breaker directly connected to it will have its rating higher+time delay.
Parallely connected loads : breaker will have max of the current rating of the given loads
series connected loads will have continuous rating + time delay increase